## 907-S-GAD-50001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Chandrahasan D | This does not comply with BMPS-A8, title block requirement. It seems that drawings are submitted without any quality checks from EPC contractor side
2 | Text Box | 1 | Chandrahasan D | This drawing to be resubmitted after revision of plot plan drawings. The plot plan of this drawing have comments which will impact contents of this drawing. This drawing looks like a layout of pipe sleeper drawing. If this is the case, Sleepers to be uniquely identiftied. -pipe line corridor to be shown - Cross over platform to be shown - fire breaks and spill containment provisions to be shown.
3 | Callout | 1 | Chandrahasan D | Include other reference drawings viz. Foundation, paving, concrete details, access roads, platform etc.