## 930-A-PID-00012-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Mahdi Ali | 356 - 6DESAL 357 - 7DESAL 358 - 8DESAL
2 | Callout | 1 | Mahdi Ali | FEED BOOSTER PUMP HOUSE
3 | Callout | 1 | Mahdi Ali | CWT
4 | Cloud+ | 1 | Khalid | corrosion inhibitor/chemical injection to be studied.
5 | Callout | 1 | Mahdi Ali | 1RHCU
6 | Text Box | 1 | Mahdi Ali | ALL TAGS FOR BUILDINGS, SATELLITE RACK ROOMS AND ELECTRICAL SUBSTATIONS ARE INCORRECT.
7 | Cloud+ | 1 | Khalid | Any lengthy repairs on these "single" pipes (supply/return) will have negative impact on all BMP units. No spare capacity is available from existing system to compensate for no. 8 chillers. These P&IDs were not Hazopped during the FEED and full Hazop to be conducted in line with project requirements.
8 | Callout | 1 | Mahdi Ali | ADD UNIT NUMBER (181)
9 | Callout | 1 | Mahdi Ali | INTERCONNECTING SYSTEMS FOR REVAMPING AREAS