## 930-Q-GAD-00001-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 |  | 1 | AutoCAD SHX Text | PUMP HSE
2 |  | 1 | AutoCAD SHX Text | AMENITY
3 | Call-out | 1 | Mahdi Ali | For various scales, always quote the PLAN scale
4 |  | 1 | AutoCAD SHX Text | SEPARATORS
5 | Text Box | 1 | Antony.Bentley | Please indicate HWL & LWL range
6 |  | 1 | AutoCAD SHX Text | ALBA HAUL ROAD
7 |  | 1 | AutoCAD SHX Text | INLET FLUMES FROM
8 |  | 1 | AutoCAD SHX Text | S/S
9 | Call-out | 1 | MAK | 930 - Interconnecting Systems - BMP Plants
10 |  | 1 | AutoCAD SHX Text | L.L.P.H TO H.L.P.H
11 | Call-out | 1 | Adel | Desal Discharge is shown under Unit 930 / interconnecting. TTSJV to discuss with Owner to verify and finalize.
12 | Text Box | 1 | Bader Abdulrahman | GENERAL NOTES FOR CONCRETE WORKS
13 | Text Box | 1 | Antony.Bentley | Access arrangement - large enough/ladder etc.?
14 | Text Box | 1 | Antony.Bentley | populate
15 | Text Box | 1 | Antony.Bentley | General : Design calculations required to confirm member dimensions & reinforcement provided.
16 |  | 1 | AutoCAD SHX Text | WS
17 | Text Box | 1 | Antony.Bentley | How will the existing pipe crossings be protected supported during these civil construction works?
18 |  | 1 | AutoCAD SHX Text | (1 HDU)
19 | Text Box | 1 | Mahdi Ali | General Comments: 1. Always indicate the Match-line drawing reference 2. Avoid using the word 'New' 3. Text shall always be in UPPER case 4. Not in Scale shall read 'NOT TO SCALE'
20 |  | 1 | AutoCAD SHX Text | MICROSCRUBBER
21 | Callout | 1 | Robert.Kawitzki | dimensions are to be millimeters typ comment
22 |  | 1 | AutoCAD SHX Text | BURIED ASBESTOS AREA
23 |  | 1 | AutoCAD SHX Text | 25° 47' 37"
24 | Text Box | 1 | Antony.Bentley | Not sufficient, drawing reference is required
25 |  | 1 | AutoCAD SHX Text | 3,4 & 5
26 | Text Box | 1 | Antony.Bentley | populate
27 | Call-out | 1 | Adel | Detailed site survey to be carried out including identifying all the underground services and incorporated in the design and drawing.
28 | Text Box | 1 | Antony.Bentley | Length
29 | Text Box | 1 | Antony.Bentley | GENERAL COMMENT: PROVISION OF EXPANSION/CONTRACTION JOINTS IN TRENCH CONSTRUCTION?
30 | Text Box | 1 | Antony.Bentley | General: hydraulic calculations required to verify slope provided
31 |  | 1 | AutoCAD SHX Text | PL'T No:-42/383
32 |  | 1 | AutoCAD SHX Text | BURIED ASBESTOS AREA
33 |  | 1 | AutoCAD SHX Text | N
34 |  | 1 | AutoCAD SHX Text | NORTH
35 | Text Box | 1 | Mahdi Ali | 2
36 |  | 1 | AutoCAD SHX Text | TRUE
37 | Text Box | 1 | Mahdi Ali | 4
38 | Text Box | 1 | Robert.Kawitzki | Complete notes
39 |  | 1 | AutoCAD SHX Text | PL'T No:-55/93
40 |  | 1 | AutoCAD SHX Text | PLANT
41 | Text Box | 1 | Mahdi Ali | 1
42 | Text Box | 1 | Antony.Bentley | Is this catchpit deep enough to contain sufficient volume of silt without requiring maintenance
43 |  | 1 | AutoCAD SHX Text | NORTH
44 |  | 1 | AutoCAD SHX Text | SKIM POND
45 |  | 1 | AutoCAD SHX Text | H.L.P.H SWITCH
46 |  | 1 | AutoCAD SHX Text | PLANT
47 | Text Box | 1 | Antony.Bentley | General : Please confirm culvert structure designed as water retaining/excluding
48 |  | 1 | AutoCAD SHX Text | FIRE PUMPS
49 |  | 1 | AutoCAD SHX Text | REMOTE H.L &
50 |  | 1 | AutoCAD SHX Text | 5 SEPERATOR
51 |  | 1 | AutoCAD SHX Text | DITCH TO GULF
52 | Text Box | 1 | Antony.Bentley | calculations/manufacturer's details required to confirm pipes structural adequacy below road
53 |  | 1 | AutoCAD SHX Text | HIGH LIFT
54 |  | 1 | AutoCAD SHX Text | PREVALING
55 |  | 1 | AutoCAD SHX Text | WIND
56 |  | 1 | AutoCAD SHX Text | FLARES
57 | Call-out | 1 | MAK | Follow BMPS-A8, the first line of the title shall state the drawing type.
58 |  | 1 | AutoCAD SHX Text | FCCU H.L FLARE
59 |  | 1 | AutoCAD SHX Text | H.L FLARE
60 |  | 1 | AutoCAD SHX Text | ALBA HAUL ROAD
61 | Text Box | 1 | MAK | General Comment: The latest drawing borders have been submitted to JV Directorate on April 2018. Please use the latest drawing borders that are part of the Homogenisation Procedure.
62 | Text Box | 1 | Antony.Bentley | Matchline continued from above
63 | Text Box | 1 | Antony.Bentley | populate
64 |  | 1 | AutoCAD SHX Text | OUTLET DITCH TO GULF
65 | Text Box | 1 | Antony.Bentley | General: Joint detail at inverted siphons needs to be fully considered/ watertight (hydrophilic strips or similar to be provided) noting this will be permanently submerged.
66 |  | 1 | AutoCAD SHX Text | S/S
67 | Text Box | 1 | Antony.Bentley | OUTFALL
68 |  | 1 | AutoCAD SHX Text | STP PLANT No:-387 BRB-219185
69 |  | 1 | AutoCAD SHX Text | The present document or drawing is property of TECHNIP ITALY S.p.A. and shall not, under any circumstances, be totally or partially, directly or indirectly, transferred, reproduced, copied, disclosed or used, without its prior written consent, for any purpose and in any way other than that for which it is specifically furnished or outside the extent of the agreed upon right of use.
70 |  | 1 | AutoCAD SHX Text | GATE
71 |  | 1 | AutoCAD SHX Text | FCCU H.L
72 | Text Box | 1 | Antony.Bentley | Is this existing channel ex. concrete? What is velocity of discharge, is scour protection required
73 |  | 1 | AutoCAD SHX Text | BRA-64535
74 |  | 1 | AutoCAD SHX Text | ROOM
75 | Text Box | 1 | Antony.Bentley | Provide wing walls at trench termination
76 |  | 1 | AutoCAD SHX Text | CHLORINATION
77 | Text Box | 1 | Antony.Bentley | General: check minimum wall thickness - external cover - 75mm horizontal bar - 12mm vertical bar - 12mm gap for concrete poker - 50mm+ min. vertical bar - 12mm horizontal bar - 12mm internal cover - 75mm total = 250mm+ > 200mm
78 |  | 1 | AutoCAD SHX Text | BRA-43696