## 932-A-PPN-80000-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | JaiMun.Oh | ALL ELEVATIONS ARE IN METERS AS PER BMPS-A1 SECTION 10.2
2 | Text Box | 1 | Syed Ahmed | Consider to provide adequate paving access for maintenance
3 | Callout | 1 | Joon Cho | No relocation to 036SSTR01 ?, SOC to confirm
4 | Text Box | 1 | Joon Cho | General Plot plan shall be updated by each unit plot plan development.
5 | Text Box | 1 | JaiMun.Oh | IPMT recommend SOC SOW shall be identified and denoted by Battery Limit or Unit Limit. Road and paving (Asphalt road/Concrete Paving/Gravel paving) need to be identified and denoted properly. Concrete pipe trench shall be shown.
6 | Callout | 1 | Syed Ahmed | Check with vendor the optimum space between the two blowers.
7 | Callout | 1 | JaiMun.Oh | QUOTE BAPCO NUMBER
8 | Callout | 1 | Syed Ahmed | Check with vendor the optimum space between the two blowers.
9 | Callout | 1 | Salman Jaffer | Provide adequate paving
10 | Callout | 1 | Syed Ahmed | 932- #3 Sulphur Plant
11 | Callout | 1 | Syed Ahmed | Consider to provide adequate paving for maintenance
12 | Callout | 1 | Syed Ahmed | Consider to provide adequate paving for maintenance
13 | Text Box | 1 | JaiMun.Oh | Shelter for Lube oil and Chemical storage : As per VOLUME 2 – COMMON DOCUMENTS AND REQUIREMENTS Section 6 / Sub-Section 6.3.3 – Civil, A covered shelter (at least 5m x 10m in area) each for lube oil and for chemical storage shall be provided at each plant or train. The shelter shall have a raised concrete paving and with provision for spill containment and coated and protected with an approved material to prevent any penetration of chemical (in case of spillage) through the concrete and into the ground. The provision of sewer system for chemical and oil storage area shall be finalized during detailed design by EPC contractor and to Owner’s approval.
14 | Text Box | 1 | Nalini Mohan | To facilitate IDD1 and 3D Model progress, the plot plan(IFR) is released with Code 2 on conditions that CONTRACTOR ensures all the comments are incorporated into the IDD1 and 3D Model (30%). Prior to 30% model review all these comments shall be incorporated and agreed with IPMT.