## 932-A-PPN-80000-002-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Joon Cho | SOC to clarify these limits on this plot plan clearly
2 | Callout | 1 | Joon Cho | No relocation TO 036SSTR01?, SOC to confirm
3 | Callout | 1 | Joon Cho | Existing (activated) UG power cable shall be shown by dot-line.
4 | Callout | 1 | Joon Cho | TOS (Top of Insert steel plate) ?, SOC to confirm
5 | Callout | 1 | JaiMun.Oh | TOS EL. to be 10000 considering road clearance of 6500 mm
6 | Callout | 1 | Joon Cho | Elevation view shall be shown and SOC to confirm head clearance as per BMPS requirement
7 | Callout | 1 | Joon Cho | Shades shall be provided (typical)
8 | Callout | 1 | JaiMun.Oh | TOS EL. 13000
9 | Callout | 1 | JaiMun.Oh | ALL ELEVATIONS ARE IN METERS AS PER BMPS-A1 SECTION 10.2
10 | Text Box | 1 | Joon Cho | <General comment> 1. IPMT recommend that Battery Limits or Unit Limits shall be denoted in order to validate with SOC SOW. 2. IPMT recommend that each Building location shall be designated & confirmed by Coordinates based Unit datum point respectively. 3. SOC to verify then confirm Building size & room arrangement as per functional requirements in consideration of future spare space. 4. IPMT recommend that Road & Paving (Asphalt road/Concrete paving/Gravel paving) shall be denoted properly. 5. IPMT recommend that elevation side view for Building shall be shown. 6. Any HOLD items or Issue Notes for potential changes/revisions shall be specified. 7. IPMT recommend that EQ List for transformer, DEG etc. shall be shown.
11 | Callout | 1 | Joon Cho | Datum point for Unit 932 ?, SOC to confirm
12 | Callout | 1 | Nalini Mohan | Highlight width of access way
13 | Text Box | 1 | Nalini Mohan | To facilitate IDD1 and 3D Model progress, the plot plan(IFR) is released with Code 2 on conditions that CONTRACTOR ensures all the comments are incorporated into the IDD1 and 3D Model (30%). Prior to 30% model review all these comments shall be incorporated and agreed with IPMT.
14 | Text Box | 1 | Joon Cho | Slope
15 | Callout | 1 | JaiMun.Oh | QUOTE BAPCO NUMBER
16 | Callout | 1 | Nalini Mohan | TOS EL. to be 10000 considering road clearance of 6500 mm