## 932-S-GAD-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Salman Jaffer | Add isolation valve
2 | Text Box | 1 | MAK | General Comment: Use the latest drawing borders that are part of the Homogenisation Procedure.
3 | Text Box | 1 | JaiMun.Oh | Model Review for Fire Fighting has not yet been performed. The layout shall be verified after model review.
4 | Callout | 1 | Salman Jaffer | This monitor may restrict the access for the Air-fin coolers
5 | Callout | 1 | Salman Jaffer | All valves should be shown on open position
6 | Callout | 1 | JaiMun.Oh | 932FHM014 shall not be located in access way.
7 | Callout | 1 | Salman Jaffer | Relocate this valve
8 | Callout | 1 | Jeung.Kim | Please make sure proper quality check as it means no such quality check has been performed.
9 | Callout | 1 | Syed Ahmed | Since this is a maintenance access, please consider to pave this area to safe the line from the heavy vehicle.(This is a common for all locations.)
10 | Callout | 1 | Salman Jaffer | Provide valve
11 | Callout | 1 | Mahdi Ali | CONSIDER CHANGING THE TITLE TO THE FOLLOWING: GENERAL ARRANGEMENT DRAWING DETAILED FIRE FIGHTING LAYOUT SULPHUR PLANTS
12 | Callout | 1 | Salman Jaffer | Add isolation valve
13 | Callout | 1 | hamad.essa | This monitor is obstructed by the staircase and cannot fully cover 049V0001
14 | Cloud+ | 1 | MAK | General Comment: -The text height is small. No need to reduce the text size, otherwise the column width shall be Increased. -Bapco Doc/Dwg No. shall be used for references in all documents and drawings.
15 | Text Box | 1 | seongjin.lee | The transmittal has been reviewed and conditionally approved as code 2 subject to the noted below; 1) Model Review for Fire Fighting System has not been performed yet. The layout shall be verified after model review. 2) The layout shall be verified again in case of any plot change. 3) All the comments noted in the data sheet shall be closed to the satisfaction of Owner in next revision.
16 | Callout | 1 | Syed Ahmed | To keep the fire line inside the unit live all the time even during isolation one source for maintenance . Please consider to provide an isolation valve in this location likes other sources.
17 | Callout | 1 | Mahdi Ali | WHERE IS SHEET 002?
18 | Callout | 1 | Mahdi Ali | INCORRECT UNIT DESCRIPTION. FOLLOW THE HOMOGENIZATION PROCEDURE
19 | Callout | 1 | Mahdi Ali | FEED DRAWING NUMBER SHALL NOT BE USED
20 | Callout | 1 | Salman Jaffer | Provide valve