## 000-A-PRO-50027-001-RA-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Mahdi Ali | Why there is 3D modelling procedure for civil only and not a unified procedure for all disciplines?
2 | Text Box | 1 | Mahdi Ali | This document shall be sent back with code 4. JV shall produce one document for all 3D disciplines including the procedure for the 3D for revamp.
3 | Text Box | 3 | Mahdi Ali | Add a procedure for Managing Revamp 3D models.
4 | Text Box | 3 | Robert.Kawitzki | BMPS-A8 shall be added
5 | Text Box | 3 | Mahdi Ali | Add BMPS-A7 as well
6 | Call-out | 3 | Mahdi Ali | In order to comment properly, 000-A-PRO-50026-001 document shall be sent for Bapco review with this current procedure.
7 | Call-out | 3 | Mahdi Ali | Document number shall not have revision. this should read 000-A-PLD-50001-001 Revision A
8 | Text Box | 4 | Mahdi Ali | The revamp is not an exception if 3D model is available. Bapco reproduced the 3D model for unit 016.
9 | Callout | 4 | Robert.Kawitzki | 3D modeling shall be provided as per Annex 1 Section 5 Item G23
10 | Text Box | 4 | Mahdi Ali | Since the FEED 3D model was based on SQL, and Bapco seed files are based on Oracle, TTSJV to ensure that no data loss occurs during the transition. In addition, all the naming rule that are defined in Bapco seed files shall be strictly followed
11 | Text Box | 4 | Mahdi Ali | and its Annexure 'Data Hanover Guide for Smart Plant Tools'
12 | Text Box | 5 | Mahdi Ali | and its Annexure 'Data Hanover Guide for Smart Plant Tools'
13 | Call-out | 5 | Hasan Al Noaimi | New control room will be built RSCB. Full ergonomics and HFID study to conducted.
14 | Text Box | 5 | Mahdi Ali | All other buildings and substations shall comply with BMPS-A8 and its annexure 'Data Handover Guide for Smart Plant tools'
15 | Text Box | 5 | Mahdi Ali | This procedure does not cover the 3D model data audit for 60%, 90% and As-built as per Bapco spec BMPS-A8 Annexure 1 'Data Handover Guide for Smart Plant Tools'
16 | Text Box | 5 | Mahdi Ali | and its Annexure 'Data Hanover Guide for Smart Plant Tools'
17 | Text Box | 6 | Mahdi Ali | Sub-systems can be added as long as it does not create a conflict with other disciplines such as piping, equipment, etc.
18 | Text Box | 7 | Antony.Bentley | All piles in as-built locations need to be included in the model
19 | Text Box | 7 | Antony.Bentley | Ducts are to be shown individually not as a grouped block; concrete surrounds are to be included where applicable
20 | Text Box | 7 | Antony.Bentley | / earthing grids
21 | Text Box | 7 | Mahdi Ali | The model content shall include all what is specified in BMPS-A8 and its Annexure 'Data Handover Guide for Smart Plant tools' without any exception. The below list is not a complete list as per Bapco specs.
22 | Callout | 7 | Robert.Kawitzki | Model content as per 30/60/90% checklist in BMPS-A8
23 | Call-out | 7 | Ali Abbas | what about direct burred cables/transit frames?
24 | Text Box | 7 | Bernard.Grace | soakaways
25 | Call-out | 7 | Mahdi Ali | Underground piping shall have line numbers as per the PIDs.
26 | Callout | 8 | Bernard.Grace | Earthing/Grounding grid, utility tie ins and lightning protection etc
27 | Call-out | 8 | Ali Abbas | Marshalling and systems cabinets, cable trays, F&G sensors, HSSD and other peripherals
28 | Callout | 8 | Bernard.Grace | Including Laboratory fume cabinets and hoods
29 | Text Box | 8 | Bernard.Grace | Equipment supports
30 | Call-out | 8 | Ali Abbas | Satellite Rack Rooms,
31 | Text Box | 8 | Bernard.Grace | Include any other element that may obstruct works
32 | Text Box | 8 | Bernard.Grace | Laboratory services (gas etc)
33 | Callout | 8 | Sankara | This includes all HV/ LV Switchgear, VFDs, Power Factor Capacitors, EMCS, UPS etc.
34 | Text Box | 8 | Bernard.Grace | Steel Framed Buildings (Workshop) are also to include - include, roof walkways, roof anchor points, wall/roof cladding including translucent sheeting, roof fans, crane rails
35 | Text Box | 8 | Robert.Kawitzki | Doors, windows, any wall penetrations, lighting, transformers, gates at transformer building openings, oil catch basins under transformers, cable trays under building up to the floor penetration, associated foot paths, roads, car parking including shades
36 | Text Box | 9 | Mahdi Ali | JV shall not add any
37 | Text Box | 9 | Antony.Bentley | and?
38 | Callout | 17 | Robert.Kawitzki | No sloped ladders are allowed as per BMPS-A8
39 | Callout | 22 | Robert.Kawitzki | Floor Grating?
40 | Text Box | 27 | Robert.Kawitzki | Different shades of grey for different slab thicknesses shall be used ie: footpath vs traffic vs heavy duty traffic (hardstands etc)
41 | Text Box | 36 | Robert.Kawitzki | Refer to BMPS-A8
42 | Callout | 43 | Robert.Kawitzki | How will the client be able to modify the model at a later stage after completion of BMP?
43 | Callout | 46 | Robert.Kawitzki | Remove JV