## 000-F-GRD-70002-001-RAP
ID N° | Subject | page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout |  | Yousif Ahmedi | 7CDU/7VDU | Updated | Y
2 | Callout |  | alexis.martinez | Correct the TAG numbers. The Atmospheric Column Heater is 010F0001 and the the Vacuum Column Heater is 011F0001 | Updated | Y
3 | Call-out |  | Ahmed Marhoon | General Instrumentation Comments applicable to fired heaters: 1. Add all applicable BMPSs such as BMPS-J33/J1/J3/J4/J5/J6/J14/J10/J15. 2. Instrument data sheets, hook ups etc. to be provided per project specs and to be developed in SPI format. 3. All BMPS standard and typical drawings to be provided to vendor. 4. Note to be added that all heaters to have access ladder and platform for all 4 inch nozzles in the stack used for PEMS or CEMS. However, nozzle location to be coordinated with the PEMS/CEMS vendors. 5. Oxygen/CO quoted to be corrected to Oxygen/Combustible. 6. For damper actuator, I/P is specified, as a standard project requirement; the actuator shall be fitted with a smart positioner as per spec and not I/P transducer. 7. It is stated that UPS is 220. The UPS power is 110V and not 220V. 8. Add Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement in case ID or FD fans are used in particular to HP Boilers. 9. Ensure instruments are supplied from AVL of BMP. 10.Narrative/flow charts/cause and effect shall be provided for any control or sequence logic. Relevant sections of the transmittal, including data sheets, issued for the furnaces to be updated accordingly. | 1. All the mentioned and applicable specifications for heater instrumentation included on SOW of Vendor or required for operation, safety, start-up, maintenance of the equipment are included in the MRQ - CONTROL SYSTEM DESIGN BASIS BMPS-J1: To be included (it is referenced in other specs, e.g. J6) - GENERAL INSTRUMENT SPECIFICATION BMPS-J2: To be included -INSTRUMENT AND ACCESSORIES TAGGING BMPS-J3: Not to be included. - INSTRUMENT WIRING IDENTIFICATION BMPS-J4: Not to be included - INSTRUMENT PIPING CLASSES BMPS-J5: Not included only Thermoskins in the scope of work - INSTRUMENTATION FOR PACKAGE UNITS BMPS-J6: To be included - WIRELESS TRANSMITTERS BMPS-J10 Not to be included. There are not Wireless transmitters in vendor scope of supply - EMERGENCY SHUT DOWN (ESD) SYSTEM BMPS-J14 0: EDS is not in vendor scope. It will not be included - MACHINE CONDITION MONITORING (MCM) SYSTEM BMPS-J15:MCM not in vendor scope, only elements according BMPS-A3 para 8:5. 2. Noted and agreed, the instruments included on vendor heater package are only the thermoskins and will be developped on SPI formta according project specs 3. MOC confirm and has included all the applicable BMPS, drawings etc applicable 4. Indicated in 12.4.12 of specification BMPS F1. Already included not necessary to repeat 5. Analyzer call has been updated. Supply not included on Heater Vendor SOW 6.Noted I/P converter deleted and updated with electropneumatic smart positioner. 7. Noted and updated according BMPS-P1 8. Machine monitoring system requirements as per BMPS-A3 para 8.5 has been included on paragraph 3.1 (engineering and services) of Material Requisition. 9. Subvendor according AVL will be defined by Procurement, as per Contract requirements there are not AVL to be followed in the Project other different than the ones already stated in datasheets. For Heater Package scope of work few instruments as Gayesco that Refracto-Pad tube skin (BMPS-SD-J-10291) are alredy indicated on data sheet 10. Noted, BAPCO comments has been implemented. | as indicated on answer
4 | Re: Call-out |  | Ali Abbas
5 | Text Box |  | Raj | Owner has reviewed and commented on the MR package submitted on Contractors request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3. | Noted | -
6 | Stamp |  | Raj
7 | Callout |  | alexis.martinez | Use 7CDU and 7VDU instead of CDU and VDU. This applies for all documents | Updated | Y
8 | Callout |  | alexis.martinez | Include a note to mention that the equipment TAG number to be confirmed | Updated | Y
9 | Call-out |  | Ali Abbas
10 | Pen |  | Ali Abbas | .
11 | Pen |  | Ali Abbas | . .
12 | Pen |  | Ali Abbas | . . . .
13 | Call-out |  | Ali Abbas
14 | Callout |  | Ahmed Ali | Decoking process | Agreed, the comment has been updated | Y
15 | Call-out |  | Hasan Al Noaimi | Decoking will not be a thermal process. It will be DDT | Decocking process shall mechanical as indicated on data sheets note. | Y
16 | Call-out |  | Hasan Al Noaimi | low NOx burner FAT | Noted, burners shall be Low NOx as required and data sheet. The test is the referred to burner workshop test to be provided by vendor before the release to site. | Y
17 | Text Box |  | Hasan Asad | Add: and equipment such as ID & FD Fan. | Updated | Y
18 | Arrow |  | Hasan Asad
19 | Call-out |  | 986131 | 7VDU shutdown with 7CDU in operating at normal and turn-down case to be checked. | Noted and updated. Heater VENDOR shall consider VDU shutdwon case. An note also are included on data sheets | Y
20 | Call-out |  | 986131 | FD Fan operating curves | Updated | Y
21 | Call-out |  | 986131 | ID Fan Operating curves | Updated | Y
22 | Call-out |  | Hasan Al Noaimi | PIMS connections as per ESIA | PEMS / CEMS connections as per ESIA is already included in the line before. For clarification and considering the reply to Bidder Query nº T381, “PEMS is the preferred monitoring method. However, during detailed design where PEMS is not feasible due to process reasons, etc, then the Bidder can propose CEMS for Owner's approval”. Therefore, PEMS will be provided but auxiliary systems for CEMS (nozzles, platform, etc.) will be supplied as well. PEMS/CEMS connections are included on scope of work of Heater Vendor. | N
23 | Callout |  | Sameer Foujdar | Provision for on-line APH cleaning to be provided. | Updated | Y
24 | Call-out |  | Hasan Al Noaimi | what about spare? | Not spare required refer to answer to comment 34 | N
25 | Callout |  | Ahmed Ali | typo mistake and | Revised | Y
26 | Text Box |  | Hasan Asad | Detailed design shall be reviewed and agreed - Double seat with preservation strategy | Detailed design of guillotines shall be clarified on tabulation phase with Heater vendors. | N
27 | Cloud |  | Hasan Asad
28 | Arrow |  | Hasan Asad
29 | Call-out |  | Hasan Al Noaimi | PEMS in the spec | verificar con HSE
30 | Call-out |  | Hasan Al Noaimi | delete if any. it has to be provided as per spec. | Updated according data sheets and specifications | Y
31 | Call-out |  | Hasan Al Noaimi | analysers in each cell | Updated according data sheets and specifications | Y
32 | Call-out |  | Jawad Alawi | add: or where metal skin point temp <350F with a risk of acid condensation | Requirement updated according BMPS-F1 para 11.4.17. requirement | Y
33 | Text Box |  | Sankara | UPS Power available for the project is at 110 V AC ( Typical) | Updated According BMPS-P1, BMPS-P16 UPS power is 115V Ac | Y
34 | Arrow |  | Sankara
35 | Arrow |  | Sankara
36 | Text Box |  | Sankara | Include HAC Drawings without which correct electrical equipment cannot be selected / offered. | Electrical requirements has been updated as follows: Minimum requirements shall be suitable for Zone 2, gas group IIC, temperature class T3. | Y
37 | Call-out |  | Tapas | Include the code: API RP 556 - Instrumentation, Control, and Protective Systems for Gas Fired Heaters | API RP 556 is a recommended practice, it shall be included as guideline to be considerd by Heater Vendor | Y
38 | Text Box |  | Ahmed Ali | to be changed to F0001 | Updated | Y
39 | Text Box |  | Ahmed Ali | to be changed to F0001 | Updated | Y
40 | Callout |  | alexis.martinez | The TAG number is 011F0001 and 010F0001. These TAG numbers to be confirmed. | Updated | Y
41 | Arrow |  | alexis.martinez
42 | Callout |  | alexis.martinez | The re is a discrepancy with the 7CDU plot plan where the Air Pre-Heater Package is located next to 7CDU Atmospheric Column Heater. | The lay out of the unit has been improved in order to face the lines from /to heater in all the passes. The layout of the unit has been updated accordingly. | N
43 | Callout |  | alexis.martinez | Change the heater description to "Atmospheric Column Heater" | Updated | Y
44 | Text Box |  | Hasan Asad | Add: with maintenance work instruction. | Updated | Y
45 | Text Box |  | Hasan Asad | Add: Detailed Rigging Study shall be provided. | Updated | Y
46 | Text Box |  | Sankara | Attach BMPS-P1, P2 to this MR, which are currently found missing | Updated
47 | Arrow |  | Sankara
48 | Text Box |  | Sankara | Query T107: Frameproof type (Ex-d) or Increased Safety (Ex-e) for HV motors. Non-sparking (Ex-n) for LV motors. | Updated accordingly | Y
49 | Text Box |  | Sankara | Ex-p HV motors are not acceptable | Updated accordingly | Y
50 | Text Box |  | Hasan Asad | Basis operation scenario, loosing the FD & ID Fans will force the heater to shutdown. Hence, capital spare consist of rotor element and electric motor shall be provided due to asset criticality. | Not applicable. In the case of loose ID fan the Heater will continue to operate cause FD fan is still in operation. If one of FD fans is loosed the other one still operating (010K0002 A/B) cause are designed 100% of design flowrate. | N
51 | Call-out |  | 986131 | Special Operation Case: 7CDU operating (either normal or turn down) and 7VDU shutdown | Updated | Y
52 | Call-out |  | Hasan Al Noaimi | is smoke test required? | Smoke test is not required | N
53 | Callout |  | Sameer Foujdar | if included APH on-line cleaning activity to be included and a procedure to be provided. | . Included in maintenance procedures. (7.14) | Y
54 | Text Box |  | Ahmed Ali | 4.5.2 10F0001 normal operation while 11F0001 is Shutdown | Updated according your comment | Y
55 | Call-out |  | Hasan Al Noaimi | Vacuum Heater Sd while the CDU is on line | Updated according your comment | Y
56 | Callout |  | Ahmed Ali | decoking | Updated according your comment
57 | Call-out |  | 986131 | what is the difference between 2.3 and 2.4. | This refer to fuel gas shutdown and pilot gas shut down. Updated on revision A | Y
58 | Call-out |  | 986131 | Pilot Gas Shutdown | not required refer to comment 41 | Y