## 021-E-DAT-00002-001-RAP-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Ravi Kumar | Refer Bid Query T1850, one of the Bidders mentioned the size of the cooler has to be increased since FEED datasheet design was found under surface. TTSJV to clarify whether the sizing basis and surface area requirements have been checked prior to issuing this datasheet
2 | Text Box | 1 | Ali Kadhem | General Comment – Applicable for some other air coolers: As per UOP EDP datasheet, inside (tube) fouling resistance (0.0020 F.ft2.h/Btu) and air side fouling resistance of (0.0020 F.ft2.h/Btu) were used. However, in this datasheet, air side fouling resistance was not mentioned. Please clarify and include.
3 | Text Box | 1 | Ravi Kumar | TTSJV to refer Bid Query T1866 and include as a Note and confirm
4 | Text Box | 1 | Ali Kadhem | General Comment: please refer to BMPS-A8 Section 4.5.1: do not indicate figures in european style (which uses commas for decimal points and periods for thousands separators), use UK/US style with periods for decimal places and commas for thousands separators. check and correct all figures
5 | Call-out | 2 | Ali Kadhem | To be written as "1.759"
6 | Text Box | 4 | Sankara | Indicate applicable Hazardous Area Classification for the electric motors: Typical