## 047-E-DAT-00001-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
2 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
3 | Cloud+ | Page 2 | Sameer.Ahmed | This length is not as per BMPS-A1 8.2.3
4 | Callout | Page 2 | Salman Jaffer | Check and confirm the heat duty on the PID is shown 29.3
5 | Text Box | Page 3 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
6 | Callout | Page 3 | Salman Jaffer | a) Please refer to Bid Query T1383 for the requirement for automatic louver b) Type 'B' manifold. c) The degree of the slop for free draining purpose per PIDs
7 | Callout | Page 3 | Julio.Aguilar | add: according to BMPS-A3
8 | Callout | Page 3 | BD Mori | To be consistent with FEED data sheet add to this note: 47E4711 shall be identical to 046E4611.