## 085-A-PFD-00001-003-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | Sameer.Ahmed | Indicate the source PFD drawing number
2 | Call-out | 1 | Mahdi Ali | Remove word 'BMP'
3 | Call-out | 1 | Mahdi Ali | Incorrect description. should be Cooling Water Tower
4 | Callout | 1 | Robert.Kawitzki | Use project abreviations. This is UG
5 | Callout | 1 | Robert.Kawitzki | What is this line?
6 | Text Box | 1 | Hasan Al Noaimi | Delete BMP
7 | Callout | 1 | Mohamed Ayyash | 085CWT0001
8 | Callout | 1 | Mohamed Ayyash | Add 085
9 | Callout | 1 | Mohamed Ayyash | 085BA0001
10 | Callout | 1 | Mohamed Ayyash | This signal comes from the HC analyzer not from FC0012
11 | Callout | 1 | Mohamed Ayyash | a missing signal line comes from the HC analyzer to this C/V
12 | Call-out | 1 | Ali Abbas | Refer to applicable comments from sheet 1
13 | Call-out | 1 | A.Jabbar Mahmood | SHALL READ "MAIN COOLING TOWER BASIN"
14 | Cloud+ | 1 | A.Jabbar Mahmood | Keep the equipment no. at the end of the descriptor
15 | Call-out | 1 | A.Jabbar Mahmood | clarify further the action of this valve inline with note 24 in the P&IDs sheet BRA-227145 (sht 7)
16 | Text Box | 1 | Ahmed Ali | Note 5 and Note 8 contradict, Note 5 to be changed to: 3 pumps are operating and 2 are spares to satisfy BMP cooling water requirement, in case of Secondary system shutdown 4 pumps required.
17 | Call-out | 1 | 986131 | Review the drain location to CSS as the water is expected to be alkaline (pH 8 - 8.5). Ensure it complies with the environmental regulations. Applied to all similar locations.
18 | Call-out | 1 | 986131 | Develop and add the symbology of Cooling tower in BMPS-A-50003.
19 | Call-out | 1 | A.Jabbar Mahmood | This is a secondary line. Apply the right line thickness.
20 | Text Box | 1 | A.Jabbar Mahmood | The indicated pressure for these streams of 22 psig seems high, unless a pressure drop in the line downstream is 22 psi! Check and confirm
21 | Call-out | 1 | 986131 | Write Cl2 instead of Cl to indicate chlorine analyser.
22 | Call-out | 1 | 986131 | In P&ID this line is shown as a existing line - Correct the deception as necessary.
23 | Call-out | 1 | Ahmed Marhoon | Location of the FI to be corrected with reference to the AG/Bu.
24 | Cloud+ | 1 | Ahmed Marhoon | A note to be added to indicate that the instruments are installed in an accessible and safe location (pit). Typical.