## 356-A-BOD-00001-001-RA-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | Page 1 | Julio.Aguilar | Document Tittle is already covered in in the row below. Unit tittle/tag to be aligned with the standardization procedure for all Process Design Basis throughout the projects for all OCs.
2 | Cloud+ | Page 1 | Julio.Aguilar | Replace "BASIS OF DESIGN" by "PROCESS DESIGN BASIS" to be consistent with the other OCs
3 | Cloud+ | Page 1 | Julio.Aguilar | Replace by Nos.
4 | Text Box | Page 1 | MAK | General Comment: Use the modified document cover pages that was transmitted to Project Mail Box to maintain the uniformity of the documents across all the OC's. Refer to, "000-A-PRO-50006-001 HOMOGENIZATION PROCEDURE - Modified Attachments"
5 | Callout | Page 1 | BD Mori | Based on the Steam, BFW and Condensate balance,FED water consumption values stated in this BOD may change. Therefore, after the FED consumption is finalised, TTSJV shall revise this BOD and resubmit for approval.
6 | Callout | Page 2 | Julio.Aguilar | Section for Acronyms/Abbreviations to be included to be consistent with other OCs. Standardization to be considered.
7 | Call-out | Page 2 | Ali Abbas | TTSJV to ensure that the package vendor follow BMPS Js specifications, standards installation drawings and AVL
8 | Call-out | Page 3 | Edgardo | Nos. 6, 7 & 8 Desalination Plants
9 | Call-out | Page 3 | Edgardo | This document is the Scoping Report done during the pre-FEED. Please confirm that this is still a valid reference for this BOD
10 | Cloud+ | Page 3 | Julio.Aguilar | remineralization
11 | Cloud+ | Page 4 | Julio.Aguilar | Nos.
12 | Cloud+ | Page 4 | Sameer.Ahmed | Only No.4 & 5 of the existing desalination plants are MED type. No.1,2 & 3 are MSF (Multi-Stage Flash distillation) type
13 | Cloud+ | Page 4 | Sameer.Ahmed | This is the FEED documents number, use the new number as PER BMPS-A8
14 | Cloud+ | Page 4 | Sameer.Ahmed | This is the FEED documents number, use the new number as PER BMPS-A8
15 | Call-out | Page 4 | Hasan Al Noaimi | GTU
16 | Callout | Page 4 | BD Mori | Post BMP PBS/1VDU will be decommissioned. Why FED consumption shown for PBS/1VDU? Chemical handling facilities will be retained in GTU. Is this FED consumption in GTU chemical handling facilities? Provide note as appropriate.
17 | Callout | Page 4 | BD Mori | 4A CDU/5CDU. 5VDU will be decommissioned.
18 | Callout | Page 4 | Salman Jaffer | Is it post BMP, please modify accordingly
19 | Cloud+ | Page 5 | Julio.Aguilar | Replace "Manufacturer" by "Supplier" to be consistent with other documents
20 | Cloud+ | Page 5 | Sameer.Ahmed | Use the final agreed unit number format: in this particular case 3H2 Plant 4H2 Plant
21 | Cloud+ | Page 5 | Julio.Aguilar | Nos.
22 | Call-out | Page 5 | Hasan Al Noaimi | Refinery South Flare
23 | Cloud+ | Page 5 | Julio.Aguilar | Flow rates to be revised base on CLCW make-up requirement
24 | Callout | Page 5 | Salman Jaffer | Review the requirement of FED for 7CDU caustic facility, SGP MEROX and KMU new train and accordingly the FED consumption to be updated.
25 | Text Box | Page 6 | Mahdi Ali | Always quote Bapco number.
26 | Callout | Page 7 | Sameer.Ahmed | (From Table 1.1.1)
27 | Callout | Page 7 | Sameer.Ahmed | (From Table 1.1.2)
28 | Callout | Page 7 | Sameer.Ahmed | (From Table 1.1.3)
29 | Cloud+ | Page 8 | Sameer.Ahmed | As per BMPS-A3 - Section 12.3 the design margin for FED is defined as "FED shall be designed to support all process units operating conditions including start-up, shut-down and T&I requirements" Therefore remove "uncertainty at FEED level stage" and modify this paragraph in-line with the BMPS-A3 Section 12.3.
30 | Callout | Page 9 | Sameer.Ahmed | Add note 2: 2) Sea water contains traces of Total Suspended Solids (TSS), Turbidity, BOD, COD and TOC.
31 | Cloud+ | Page 12 | Julio.Aguilar | Capacity of the desalination plant is depending on the overall water requirement for BMP units. The BMP units overall water balance is not finalized yet.Therefore base on the overall water balance TTSJV shall review the capacity of the desalination plants.
32 | Callout | Page 13 | Sameer.Ahmed | Instrument Air
33 | Cloud+ | Page 15 | Julio.Aguilar | Supplier
34 | Cloud+ | Page 15 | Julio.Aguilar | Please check and confirm these figures for the sea water supply to the unit with the latest BMPS-A1