## 085-S-DAT-00014-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | MAK | COOLING WATER TOWER OR CWT for short form. This change shall be reflected globally. | Noted. It will be implemented in next revision. | Y
2 | Text Box | 1 | MAK | The correct document template (cover page and format) shall be used. MOC shall coordinate with the Directorate for the correct template. | Cover page and format is under preparation by JV Directorate. It will be implemented later. | N
3 | Text Box | 1 | Raj | Owner has reviewed and commented on the MR package submitted on Contractors request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3. | Noted | Y
4 | Text Box | 4 | Ahmed Marhoon | The following are comments related to instrumentation and control. These comments are also applicable for 085-S-DAT-00015 issued as part of this Transmittal. 1. The package contains Air Blowers. Add a clear note on Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement. Requirement of MCM to be verified with the supplier. Reference to BMPS-J15 MCM to be added. 2. Instruct the supplier to source instrumentations from project AVL onl. 3. Add a note to the supplier with reference to the applicable BMPS to design and supply the system according to the final PID. Functional design specifications covered in this document shall be firmed based on the approved PID. Vendors to be clearly notified on the necessity to include all the Hazop3/SIL recommendations and changes made Post-EPC-Development. 4. TTSJV is requested to ensure that all the specific technical/functional requirements are covered and detailed in the requisition specification that will be sent out to suppliers. In case this document would be the only one for MR, then all the relevant BMPS to be included in the Data Sheet notes. 5. Suppliers to be notified on the possibility of considering wireless instruments for non-critical monitoring devices. Reference to BMPS-J10 Wireless to be added if applicable and meeting the criteria (under development) of wireless measurement. 6. All the machinery monitoring probes etc. shall be factory fitted by the vendor and not at site. 7.Narrative/flow charts/cause and effect shall be provided for any control or sequence logic. 8. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting &etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31. 9. In addition to BMPS-J6, all applicable BMPS from J class to be added for the supplier to comply with. e.g. J2, J3, J15 ... etc. All instruments and control systems to be designed according to BMPS specifications. 10. Supplier to be instructed to generate all instrument data sheets, hook ups ...etc. in project specs (according to Bapco standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included 11. Supplier to comply with all the applicable BMPSs and provide, as a minimum, all the documents, hardware, software and services according to the relevant sections of the BMPSs in the agreed standard formats of the project. List to reflect all the required deliverables in accordance to BMPS J series. 12. Vendor/TTSJV shall provide a list of deviation from BMPS specifications, in addition to the requisition specifications, for owner's review and approval. | 1. The package Air Blowers are auxiliary equipment with small size, therefore, MCM is not applicable. 2. AVL for instrument is included in MRQ. See attachment in document 000-S-GRD-70001-001 3. Applicable BMPS's are included in 000-S-MRQ-70001-001. JV Directorate will check and include any additional specification as required. If needed Hazop to this package, vendor will be informed and scenarios evaluated during hazop sessions will be considered by package vendor. Currently for this package Hazop is not required. 4. See reply to point 3 5. It is under discussion with JV Directorate (instrumentation) Vendor will be informed with final decission to standardize which instruments are required wireless. 6. Machinery Monitoring not required for this equipment. (Air blowers have small size) 7. Applicable Vendor documentation is included in 000-S-SOW-70001-001 part II 8. See reply to point 3 9. See reply to point 3 10.Noted. Vendor is informed that Project templates shall be followed (Refer to notes in 000-S-SOW-70001-001 part II). Vendor is informed that project hook-ups (to be provided later) shall be followed (Refer to Instrument section in 000-S-GRD-70001-001) 11. See reply to point 3 and point 10. 12. Deviation List from BMPS specification is required in Material Requisition | N&Y
5 | Cloud+ | 5 | A.Jabbar Mahmood | Clarify the statement. | According to P&ID and FEED data sheet, backwash shall be initiated when the flowrate totalizer value is more than a specified value. | Y
6 | Cloud+ | 5 | A.Jabbar Mahmood | Clarify this statement. | According to P&ID and FEED data sheet, backwash shall be initiated when the flowrate totalizer value is more than a specified value. | Y
7 | Text Box | 6 | Mahdi Ali | Equipment tag is not as per BMPS-A8 | Basin tag has been changed to 085BA0003 | N
8 | Call-out | 6 | A.Jabbar Mahmood | As per the PFD, the basin is numbered as 085BA0002. Check and update | Correct tag is 085BA0003. PFD shall be updated. | N
9 | Call-out | 6 | Ahmed Marhoon | How will the local control be achieved? The current revision of PID does not indicate this requirement. Will a local hand switch be provided at the field? or the idea is to have a manual reset on the solenoid valves? Also, what are the safety measures that will be in place during the manual control/sequence mode? The control system design shall be capable of allowing this operation and ensure a Bumpless transfer design is in place. | Final control system description to be defined in a later stage, once technical offers are received. | N
10 | Call-out | 6 | alexis.martinez | Page 6. The first item is written as there are many causes to shutdown or inhibited the back wash cycle, but there is only one cause. Re-write the paragraphs to correct them. | Noted. It will be implemented in next revision. | Y
11 | Cloud+ | 7 | A.Jabbar Mahmood | As per the H&MB data, the design flow rate is 4000 USgpm. Check, confirm and update documents (PFD, P&IDs, etc) accordingly | Capacity has been updated according to estimated utility information. To be confirmed once TTSJV has defined consumptions. H&MB and PFD will be updated accordingly | N
12 | Cloud+ | 7 | A.Jabbar Mahmood | As per the PFD, the pressure at the inlet of the flow control valve is 76 psig. Accordingly the pressure at the inlet of the filter is expected to be less than 76 psig. Check and update accordingly the appropriate documents. | Pressure has been revised and calculated hydraulically with current information. PFD will be updated accordingly. | N
13 | Cloud+ | 7 | A.Jabbar Mahmood | Advise the basis of the max allowable pressure drop of 36 psi. | This maximum allowable pressured drop has been defined according to hydraulic calculation results performed by Process department. | Y
14 | Call-out | 7 | 986131 | Add: "per filter" | Noted. It will be implemented in next revision. | Y
15 | Text Box | 8 | Sankara | BMPS-P2 and not P3 deals with hazardous area calssification | Requirements regarding Ex protection are included also in BMPS-P2. BMPS-P3 is not applicable to this scope and is not included in 000-S-MRQ-70001-001 | N
16 | Call-out | 8 | A.Jabbar Mahmood | The targetted TSS at the outlet of each filter shall be specified and guaranteed. | TSS required is 30 ppm normal / 35 ppm maximum. As indicated in Basis of Design. | N
17 | Cloud+ | 8 | 986131 | Review the TDS and Chloride based on the chemical dosing to the cooling tower and update. | This information has already been revised and updated according to the Basis of Design. | N
18 | Call-out | 8 | 986131 | Add in 3.5.: - Maximum pressure drop at normal water flow expected after backwash - Minimum operating time for the filter. - If the filter media is replaceable cartage then life of filter to be guaranteed. | Minimum operating time for the filter (21 hours) already required in design conditions. This is not a process guarantee indicated in Basis of Design Maximum pressure drop at normal water flow expected after backwash to be requested to Vendor and included in section 3.3 (Operating and Design conditions).Filter media is not replaceable cartridge | N
19 | Call-out | 9 | Ebrahim | and General Design Rules for Electrical System, BMPS-P1 | BMPS-P3 will be included instead of BMPS-P1. BMPS-P1 has not been included in 000-S-MRQ-70001-001 | N
20 | Text Box | 10 | Ahmed Ali | During normal operation, 7 filters must be sufficient to filter 3% of operating circulating flow rate. One filter can be put of service for maintenance during normal operation | Noted.It will be implemented in next revision. | Y
21 | Call-out | 10 | Ahmed Marhoon | Mixing of electrical and instrument component/signals is against the BMPS standard. HV electrical equipment shall be completely segregated from the LV control equipment. Junction boxes dedicated for instrumentation shall be designed and supplied in compliance with the BMPS specifications. This bullet to be amended accordingly. | Noted. It will be implemented in next revision. | Y
22 | Call-out | 10 | 986131 | access for removing and replacement of filter element / media. If a media is used then proper dump nozzles to be provided. | Scope indicated in Data Sheet is a general scope. This requirement will be added in MRQ. (000-S-GRD-70001-001).Nevertheless, following paragraph has been included: "...easy access for filter media replacement." in Manufacturer scope section. | Y
23 | Call-out | 10 | 986131 | Filter maintenance procedure - In case of cartage - provide replacement method. Method to dispose the cartage in accordance with the local environmental law to be provided. And if acid cleaning of other methods are to be employed provide the details. In case of media - provide procedure of unloading and loading the filter media. Method statement to safely dispose the media to be provided in accordance with the local law. Note: In case special cleaning procedure are to be employed (say acid cleaning etc.) adequate arrangement to be made to facilitate the same. | Noted. The following paragraph will be included: "MFR to provide procedure of unloading and loading the filter media". Any further instructions and requirements for correct operation and maintenance of package will be included in process philosophy and installation and operation manual. | Y
24 | Call-out | 10 | 986131 | Effluent generated, Including any sold waste that may be generated during bed/cartage replacement. | MOC: Noted. The following wording will be included: "MFR to provide information regarding effluent generated in SIDE STREAM FILTERS , Including any sold waste that may be generated during according to 000-A-PRI-50004-001" | Y
25 | Call-out | 10 | 986131 | Consider providing platform for safe and ease of filter cartage/filter media replacement. | Scope indicated in Data Sheet is a general scope.For more detailted scope please refer to MRQ. (000-S-SOW-70001-001) The need of platform will be checked during tabulation stage once preliminary drawings are received. It is mentioned also in MRQ. (000-S-GRD-70001-001). | N
26 | Call-out | 10 | Sameer Foujdar | Consider to provide a permanent platform for operating MOV during backwash Operation. | There are not MOV within Vendor Scope. | N
27 | Callout | 11 | alexis.martinez | On page 11, Table 5.1, review the operating conditions and confirm. They are inconsistent with the conditions show on PFD and FEED document 2520-u085-SP-4230-01 | This information has been updated according to the latest information. PFD will be updated accordingly. | N
28 | Call-out | 12 | Ahmed Marhoon | The table included does not cover all the piping material classes requirements. For instance, the material class and thickness of impulse tubing is not mentioned. According to BMPS-J2/J6, SS316 is to be considered for the instrument impulse tubing. In addition to the table, a reference to the applicable BMPS standard to be added in order to capture all the specifications requirements. This is a typical comment for similar sections on all transmittals where only a portion of the BMPS specification is extracted and included in the materials specifications. | This is a data sheet and only main applicable Specifications have been added. For all applicable specifications please refer to MR. ( 000-S-MRQ-70001-001). JV Directorate will check and include any additional specification (if applicable) | N
29 | Call-out | 13 | MAK | General Comment: Bapco's Document/Drawing numbers shall be used for all references. | New P&ID project numbers will be included when available. | N