## 000-G-GRD-70001-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Ahmed Marhoon | The following are comments related to instrumentation and control. Contractor is requested to update the other documents issued as part of this transmittal based on the comments stated herein and ensure consistency prior to release of MR to suppliers. 1. Add a clear note on Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement. Requirement of MCM to be verified with the supplier. Reference to BMPS-J15 MCM to be added. 2. Instruct the supplier to source instrumentations from project AVL only. 3. Add a note to the supplier with reference to the applicable BMPS to design and supply the system according to the final PID. Functional design specifications covered in this MR shall be firmed based on the approved PID. Vendors to be clearly notified on the necessity to include all the Hazop3/SIL recommendations and changes made Post-EPC-Development. 4. Minimum Flow arrangement/design shall be reviewed and confirmed by the supplier. Contractor to consider the pumps protection and process requirements according to manufacturer and licensor recommendations. 5. Supplier to be notified on consideration of ESD interlock and Permissive (linked to MOV open status) requirements per the PID. 6. Suppliers to be notified on the possibility of considering wireless instruments for non-critical monitoring devices. Reference to BMPS-J10 Wireless to be added if applicable and meeting the criteria (under development) of wireless measurement. 7. All the BN machinery monitoring probes etc. shall be factory fitted by the vendor and not at site. 8. Narrative/flow charts/cause and effect shall be provided for any control or sequence logic. 9. Scope of supply for the interposing relays to be clearly defined. 10. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting &etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31.
2 | Text Box | 1 | Ahmed Marhoon | 11. In addition to BMPS-J6 and J2, all applicable BMPS from J class to be added for the supplier to comply with. e.g. J3, J15 ... etc. All instruments and control systems to be designed according to BMPS specifications. 12. Supplier to be instructed to generate all instrument data sheets, hook ups ...etc. in project specs (according to Bapco standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 13. Compliance to licensor's mandatory and recommended requirements to be included. 14. Contractor is requested to validate the models quoted for the instrumentation and ensure that the latest models are supplied for BMP in accordance to the projects specifications. To avoid supplying an obsolete and/or products at their obsolescence phase, vendors to be instructed to provide Products Life-Cycles/Road-maps. For example, model YTA310 for ESD Transmitter has recently announced obsolete and needs to be replaced with the latest model number. This is a general comment that need to be globally addressed by the contractor. 15. Supplier to comply with all the applicable BMPSs and provide, as a minimum, all the documents, hardware, software and services according to the relevant sections of the BMPSs in the agreed standard formats of the project. List to reflect all the required deliverables in accordance to BMPS. 16. Inspection and Test Plan to include the participation of the client in accordance with the BMP agreed procedures. Loop testing plan to be detailed.
3 | Call-out | 1 | Ahmed Marhoon | Add applicable tag numbers.
4 | Text Box | 1 | Raj | Owner has reviewed and commented on the MR package submitted on Contractors request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3.
5 | Text Box | 2 | Mahdi Ali | Always add title in the header
6 | Callout | 3 | Isamu | This to be listed as the last in the order of the technical priority,
7 | Callout | 3 | Isamu | Please define this (Recommissioning and commissioning ???
8 | Callout | 3 | Adnan Alothman | As per the Contract, Annex1-Technical documents do not have any order of precedence. Please correct this to align with EPC Contract.
9 | Call-out | 4 | Ali Abbas | All BMPS J Class specifications, typical and standard drawings and AVL to be included.
10 | Text Box | 4 | Hasan Asad | As specified in G9, the seal supplier shall consider High Consequence Pump for seal and API system selection. The basis of design shall be provided for purchaser review and approval.
11 | Call-out | 5 | Ali Abbas | 1. Any deviation from BMPS-A3 section 8.5 MCM and other BMPS J spec to be listed for owner review and approval. 2. The probes for radial and axial shall meet the BN system as per BMPS-J15.
12 | Text Box | 5 | Hasan Asad | Basis BMPS-A3, 3X axial probes.
13 | Callout | 6 | Mohamed Ayyash | What is the difference ?
14 | Text Box | 6 | Hasan Asad | Pump LCCA for X years shall be provided with proven reliability data to be used as input to maintenance strategy and equipment purchase.
15 | Callout | 6 | Adnan Alothman | For all critical equipment like BB5 Pumps, company representative attendance is required as per BMPS-B11.
16 | Text Box | 6 | Adnan Alothman | LCCA report shall be provided as required by BMPS-A7.
17 | Callout | 7 | Isamu | but anchor bolts size, type, projection and quantity shall clearly be provided on GA drawings
18 | Call-out | 7 | Ali Abbas | Add Owner Respresentative
19 | Call-out | 7 | Ali Abbas | Add vendor involvement in CHAZOP
20 | Call-out | 7 | Ali Abbas | and I-FAT
21 | Call-out | 7 | Ali Abbas | J Material Deliverables to meet project spec requirements and CDRL
22 | Cloud+ | 7 | Ahmed Marhoon | These activities are major milestones for the package and it is mandatory to be attended by Client representatives. Attendees list to be updated based on the agreed project matrix.
23 | Call-out | 7 | Ahmed Marhoon | Add ESD/MCM as applicable.
24 | Callout | 8 | Isamu | Delete
25 | Text Box | 10 | Hasan Asad | Add: API 570 for High Consequence Pump identification.
26 | Callout | 11 | Isamu | Replace with: NPSHR test shall be carried out with performance test and the number of points shall be same as the number of flow rate points. NPSHR curve shall be plotted on the perfromance curve at all stages of curve submission.
27 | Pen | 15 | Isamu | _
28 | Pen | 15 | Isamu | _
29 | Pen | 15 | Isamu | _
30 | Callout | 15 | Isamu | his
31 | Callout | 15 | Isamu | to his
32 | Callout | 15 | Mohamed Ayyash | Should read " Commissioning and Start-up " not vise versa
33 | Callout | 15 | Mohamed Ayyash | Add "Commissioning"
34 | Callout | 16 | Isamu | Please replace this confusing phrase with " Per each item or Tag No. Also make clear why driver (electric motor require spare rotor?.
35 | Callout | 16 | Mohamed Ayyash | Need to be clear if this includes Commissioning phase ?
36 | Text Box | 16 | Hasan Asad | Consumables for lube oil and cooling water flushing shall be provided.
37 | Text Box | 16 | Hasan Asad | With preservation strategy.
38 | Text Box | 16 | Hasan Asad | General Requirement: Mechanical Seal filling cart to be provided. The cart shall be designed to be capable for filling requirement per unit.
39 | Text Box | 17 | Hasan Asad | The Supplier Specialist shall be experienced with installation and erection, commissioning and troubleshooting and machine condition monitoring surveillance.
40 | Call-out | 20 | Ahmed Marhoon | It has been brought to our knowledge that Yokogawa model YTA310 ESD Transmitter is obsolete. Contractor is requested to validate the models quoted for the instrumentation and ensure that the latest models are supplied for BMP in accordance to the projects specifications. To avoid supplying an obsolete and/or products at their obsolescence phase, vendors to be instructed to provide Products Life-Cycles/Road-maps.