## 010-E-DAT-00030-001-RAP-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | MAK | General Comment: Use the modified document cover pages that was transmitted to Project Mail Box to maintain the uniformity of the documents across all the OC's. Refer to, "000-A-PRO-50006-001 HOMOGENIZATION PROCEDURE - Modified Attachments"
2 | Text Box | Page 1 | 986131 | Use the revised equipment number in the data sheet.
3 | Text Box | Page 1 | 986131 | Refer API 661: The data sheet is incomplete - provide the sheet 2 of 2 of API data sheet. And the purchase check list duly filled.
4 | Callout | Page 1 | Mohamed Ayyash | 7CDU ( apply to all sheets)
5 | Cloud+ | Page 1 | Mohamed Ayyash | General comment: Many figures are written in a very small font. text font to be standardized, clear & visible
6 | Callout | Page 1 | Mohamed Ayyash | No. (Typo) apply to all sheets
7 | Callout | Page 2 | Adnan Alothman | Inlet Oper. Press. is 115 as per FEED Data Sheet. Verify & confirm
8 | Callout | Page 2 | Mohamed Ayyash | enlarge font (all the marked clouds, can hardly see them)
9 | Call-out | Page 2 | 986131 | The duty of the exchanger has a large variation: PFD design = 8.5 MMBTU/hr PFD design turn down = say 50% of above. Alternate case = 17.6 MMBTU/hr Exchanger design case = 49.3 MMBUT/hr The duty varies from 8.6% to 100%. Provide adequate control to vary the air flow to meet the wide range of operating condition
10 | Text Box | Page 2 | 986131 | Note and numbers are currently not distinguishable. please mark the notes in a different manner to distinguishable Example: Write the notes with in square bracket "[1]" while the number shown in FPS unit can retail "()"
11 | Call-out | Page 2 | 986131 | Provide a separate data sheet for the PFD design case. and add a note: Minimum Flow Rate with unit at turndown: 50% of aircooler normal flowrate.
12 | Call-out | Page 2 | 986131 | Provide the detailed calculation how the design pressure was arrived at,
13 | Call-out | Page 2 | 986131 | Bundle to be self draining. Provide adequate notes for the same.
14 | Call-out | Page 2 | 986131 | Data cannot be validated with out the hydraulics of the circuit.
15 | Callout | Page 2 | alexis.martinez | Equipment Number need to be updated as per the new numbering provided by owner.
16 | Callout | Page 2 | alexis.martinez | Number of bays are not matching with FEED data sheet. Calculations to be provided
17 | Callout | Page 2 | alexis.martinez | Increase the size of the letters.
18 | Callout | Page 2 | alexis.martinez | Allowed pressure drop on tube was increase compared with FEED value. Calculations to be provided
19 | Cloud+ | Page 3 | Adnan Alothman | In note 10; Add "-" to the pressure to be (-10psig)
20 | Call-out | Page 3 | Ahmed Marhoon | Scope of supply for the instrumentation to be clarified. Accordingly, reference the required BMPS-J class specifications. Requirements and specification for the VSHs and TGs to be detailed according to the BMPS, vendor design and approved PID. Other DCS functions and field hardware (such as switches) to be captured according to the PID. These comments are also applicable for 010-E-DAT-00032-001-RAP.
21 | Text Box | Page 3 | Hasan Asad | Fan and motor bearings lubrication points to be extended to platform level.