## 083-S-DAT-00001-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
2 | Call-out | 1 | Mahdi Ali | Nitrogen Plant Unit number was changed from FEED from 342 to 083
3 | Callout | 1 | BD Mori | As indicated in the Basis of Design, the nitrogen consumption values are estimated only and EPC contractor need to develop the detail nitrogen balance . Therefore, before placement of the purchase order for Nitrogen Plant, TTSJ shall finalize the nitrogen consumption to arrive at the Nitrogen Plant capacity.
4 | Callout | 2 | Julio.Aguilar | Please, consider a dedicated Section for Acronyms/Abbreviations to be consistent with other OCs. Standardization procedure to be considered.
5 | Callout | 3 | Julio.Aguilar | Please, consider a dedicated Section for Acronyms/Abbreviations to be consistent with other OCs. Standardization procedure to be considered.
6 | Callout | 3 | Syed Ahmed | check unit number
7 | Callout | 3 | Dowon Pyun | This is detail engineering stage and Contractor is prohibited from using ambiguous phrases such as 'Preliminary', 'Estimation', 'Possibility', etc. on the requirements of data sheets. It is Contractor's responsibility to verify FEED documents and fix the data requirement at the earliest.
8 | Callout | 4 | Salman Jaffer | at LSDP
9 | Callout | 4 | Salman Jaffer | including LBOU
10 | Callout | 4 | Salman Jaffer | at LSDP
11 | Callout | 5 | Julio.Aguilar | Number of absorbers to be confirmed. e.g. Two 100%
12 | Callout | 5 | balagangadhar.k | section
13 | Callout | 5 | BD Mori | normal and
14 | Text Box | 5 | Dowon Pyun | Contractor to confirm if suction air filters are required and it is in Supplier's scope.
15 | Callout | 5 | Salman Jaffer | at LSDP
16 | Callout | 5 | Salman Jaffer | Delete
17 | Callout | 5 | Salman Jaffer | ADD; LSFO and south process section will be fed from new nitrogen system from BMP
18 | Callout | 6 | BD Mori | The supplier shall ensure that the overpressure relief valve or control valve vent provided on the nitrogen storage vessels or any other location withing the plant are routed to appropriate place. It is not permitted to route the vents to atmosphere. This is required to prevent safety hazards, loss of nitrogen to atmosphere and prevention of high noise associated with the venting.
19 | Callout | 7 | balagangadhar.k | section
20 | Callout | 7 | BD Mori | peak demand and
21 | Callout | 7 | BD Mori | Vendor shall advise how to monitor CO and H2 in nitrogen product on real time basis similar to O2, CO2 and H2O specified here?
22 | Cloud+ | 8 | Julio.Aguilar | Confirm units ppm or vppm to be consistent
23 | Callout | 8 | balagangadhar.k | section
24 | Callout | 8 | balagangadhar.k | section
25 | Callout | 8 | balagangadhar.k | section
26 | Callout | 9 | Salman Jaffer | except one SGP and one ARU
27 | Callout | 9 | BD Mori | Supplier will not be aware of these abbreviation. Define GAN and LIN.
28 | Callout | 10 | Julio.Aguilar | 40% turndown shall be confirmed by the package supplier
29 | Callout | 10 | BD Mori | Refer bid technical query T493. TTSJV shall review and update this value and all the other values in this document as required.
30 | Callout | 10 | BD Mori | Refer bid query T335: Feasibility of reducing the operating pressure of the existing N2 facility at LSDP, as well as carrying out the necessary hydraulic and mechanical check for the integration of the new/existing systems shall be done by EPC contractor.
31 | Callout | 10 | BD Mori | Total of a+b+c+d = 177380 lb/hr. Please check and update as required.
32 | Callout | 11 | balagangadhar.k | Check borders for all tables
33 | Callout | 11 | Salman Jaffer | Include site conditions data as per sections 6.2 and 6.3 of revised BMPS A-1.
34 | Cloud+ | 12 | Julio.Aguilar | Replace by "SUPPLIER"
35 | Callout | 12 | Salman Jaffer | The information provided in the FEED duty specification has been deleted such as: " as a heating medium ambient air is to be preferred against steam, i.e airfin vs steam driven exchangers shall be used. If convenient, electrical heaters can be provided inside the system." This is an important information. Therefore, please incorporate the relevant notes here.
36 | Callout | 13 | balagangadhar.k | section
37 | Callout | 13 | Salman Jaffer | Refer to Bid Query T335 for the feasibility of reducing the operating pressure of the existing N2 facility at LSDP, as well as carrying out the necessary hydraulic and mechanical check for the integration of the new/existing systems
38 | Callout | 13 | Dowon Pyun | All piping materials shall be met with BMPS-L2 as minimum, whatever applicable