## 085-A-PFD-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | Sameer.Ahmed | Indicate the source PFD drawing number
2 | Text Box | 1 | MAK | Follow the General Comments which were given in transmittal BMP-MOC-TRI-00033 for (010-A-PFD-00001-001 )
3 | Call-out | 1 | MAK | COOLING WATER TOWER
4 | Call-out | 1 | Mahdi Ali | This to indicate total sheet numbers
5 | Callout | 1 | Robert.Kawitzki | Equipment numbers shall be shown - typical comment
6 | Callout | 1 | Robert.Kawitzki | Unit number as per project documentation - typical comment
7 | Text Box | 1 | Hasan Al Noaimi | Delete BMP
8 | Text Box | 1 | Hasan Al Noaimi | Delete BMP
9 | Callout | 1 | Mohamed Ayyash | Unnecessary break
10 | Call-out | 1 | Ali Abbas | specify LC XXXX number
11 | Call-out | 1 | Ali Abbas | show arrow direction and SP at correct arrow location
12 | Call-out | 1 | Ali Abbas | Suggest to add a note near these valves to clarify the function and logic
13 | Call-out | 1 | Ali Abbas | AI for PFD representation. General Comment
14 | Call-out | 1 | Ali Abbas | AI Not AIT for PFD representation
15 | Text Box | 1 | A.Jabbar Mahmood | The calcite beds are actually shown in a "row" in the P&IDs while they are represented in a different arrangement in PFDs. The right arrangement shall be represented in PFDs.
16 | Text Box | 1 | A.Jabbar Mahmood | The bed vessel shapes are represented differently in the P&IDs than in PFDs (flat versus elliptical head. TR to ensure consistency.
17 | Call-out | 1 | A.Jabbar Mahmood | General: Use a consistent representation of the pressure and temperature blocks i.e. the circle above the rectangle
18 | Text Box | 1 | A.Jabbar Mahmood | The indicated pressure for streams 11 and 19 of 22 psig is not consistent with that of streams 79 and 80 (0 psig), unless a pressure drop is assumed across an inject quil of 22 psi! Check and confirm
19 | Call-out | 1 | A.Jabbar Mahmood | According to the H&MB and design basis, 10% of the "total CW make flow rate" is routed through the calcite beds. However, stream "B" does not represent the total make flowrate (total less the amount routed to the calcite beds) and hence A/B ratio will not be 10% (higher than 10%). TR to check and amend as necessary. Also rephrase the note for clarity. review the viability of relocating the F0005 to stream 1 to give direct measurement of the total Make-up flow and direct control of the flow ratio.
20 | Text Box | 1 | A.Jabbar Mahmood | General: the descriptor text shall be "left" justified
21 | Cloud+ | 1 | A.Jabbar Mahmood | Add ".... TO MAIN COOLING TOWER BASIN BA0001"
22 | Cloud+ | 1 | A.Jabbar Mahmood | TITLE OF SHEET1 SHALL READ "MAIN CALCITE BED PACKAGE"
23 | Call-out | 1 | A.Jabbar Mahmood | "...TO MAIN COOLING TOWER BASIN..."
24 | Call-out | 1 | 986131 | break the secondary line - preferably the break to be in the vertical line as per BMPS A3. Consider relocating the main line suitable to achieve the above objective.
25 | Call-out | 1 | 986131 | Review the drain location to CSS as the water is expected to have a very low pH (2). Ensure all the down stream equipment and piping are designed to handle the acidic water. Ensure it complies with the environmental regulations. Applied to all similar locations.
26 | Call-out | 1 | 986131 | What does these two new legends mean. Any line that are shown as "existing" must be reverted back as regular lines at the end of project. Cover it with a general note.
27 | Cloud+ | 1 | A.Jabbar Mahmood | Consider moving the main line to left side of the secondary line and break the secondary line instead.
28 | Text Box | 1 | A.Jabbar Mahmood | Ensure that the numbering of the equipment in the packages are numbered in a sequential manner with respect to the process flow direction, in consultation with the owner.