## 000-F-GRD-80003-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout |  | Mohamed Ayyash | page 1/20, correct all pages
2 | Call-out |  | Ahmed Marhoon | The following are general comments related to instrumentation and control. All relevant sections of this transmittal to be updated accordingly. 1. In addition to BMPS-J6, all applicable BMPS from J class to be added for the supplier to comply with. e.g. J2, J3, J9 ... etc. All instruments and control systems to be designed according to BMPS specifications. 2. Supplier to be instructed to generate all instrument data sheets, hook ups ...etc. in project specs (according to Bapco standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. 3. Add a note on the nozzle location for CEMS to be coordinated/finalized with the CEMS vendors. 4. The transmittal does not exactly reflect the scope of supply captured in FEED PID. This gap to be addressed/clarified. 5. Add Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement. 6. Supplier to be instructed to source all instrumentation from the approved AVL for BMP. 7. List of documents, hardware, software and services to comply with the BMPS specifications (including tests and certifications). 8. Add a note to the supplier with reference to the applicable BMPS to design and supply the system according to the final PID. Also supplier to note that the the design is subject to changes based on Hazop/SIL/CHAZOP studies. 9. Reference to BMPS-J10 Wireless to be added. Supplier to be notified on the criteria being development for instruments that can be accepted as wireless for non-critical measurement. 10. Compliance to licensors mandatory and recommended requirements to be included.
3 | Stamp |  | Nalini Mohan
4 | Text Box |  | Nalini Mohan | Owner has reviewed and commented on the MR package submitted on Contractors request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3
5 | Call-out |  | Ali Abbas | 11. Narrative and Flow chart for Incinerator start-up and shutdown sequence to be provided in addition to control narrative.
6 | Ellipse |  | Mohamed Ayyash
7 | Callout |  | Mohamed Ayyash | correct page numbers
8 | Arrow |  | Jeung.Kim
9 | Text Box |  | Jeung.Kim | Add Purchaser also
10 | Callout |  | Mohamed Ayyash | delete :
11 | Callout |  | Mohamed Ayyash | move to next page on all documents
12 | Call-out |  | Ahmed Marhoon | Add CHAZOP
13 | Call-out |  | Ahmed Marhoon | Correct abbreviation to "ESD".
14 | Call-out |  | Ahmed Marhoon | What about SAT?
15 | Cloud |  | Ahmed Marhoon
16 | Call-out |  | Ahmed Marhoon | These activities are major milestones for the package and it is mandatory to be attended by Client representatives. Attendees list to be updated based on the agreed project matrix.
17 | Call-out |  | Ahmed Marhoon | This is not a loop test. This is an IFAT.
18 | Text Box |  | Salman Jaffer | The stack high in this sheet is not consistence with data sheet (044-F-DAT-00001-001) page 9 of 10. Using either actual hight or minimum requirement. In this sheet H=167 and in the other document H=165 min.
19 | Arrow |  | Salman Jaffer
20 | Text Box |  | Salman Jaffer | In the PID nomenclature is Air Blowers
21 | Arrow |  | Salman Jaffer
22 | Text Box |  | Salman Jaffer | Independent air intake duct is required. Refer to PID BRA-226708 sheet 1 of 1
23 | Arrow |  | Salman Jaffer
24 | Callout |  | Syed Ahmed | To prevent vibration of the power supply junction box for the blower motor, the box shall be installed on the separate base plate .
25 | Call-out |  | Ahmed Marhoon | or according to the SIL requirement.
26 | Callout |  | Salman Jaffer | Including platform for access to filter for maintenance
27 | Line |  | Mohamed Ayyash
28 | Callout |  | Mohamed Ayyash | need to be consistent, either put a full stop at the end of all sentences or not.
29 | Arrow |  | Mohamed Ayyash
30 | Line |  | Mohamed Ayyash
31 | Callout |  | BD Mori | jacketing,
32 | Text Box |  | Salman Jaffer | Please refer to the comments regarding providing spare burner.
33 | Arrow |  | Salman Jaffer
34 | Text Box |  | Salman Jaffer | Please add pre-commissioning and commissioning procedures including the curing procedure.
35 | Arrow |  | Salman Jaffer
36 | Callout |  | BD Mori | This is not optional. It is required.
37 | Line |  | Mohamed Ayyash
38 | Line |  | Mohamed Ayyash
39 | Line |  | Mohamed Ayyash
40 | Cloud+ |  | Ahmed Marhoon | Not all instruments have been listed in this document. According to the FEED PID, Incinerator vendor to supply analyzers, ESD Valves ...etc and those could not be seen in this transmittal. TTSJV to clarify.
41 | Callout |  | Nalini Mohan | Include for process guarantees refer to incinerator datasheet
42 | Text Box |  | Salman Jaffer | Please add air intake filters
43 | Callout |  | BD Mori | Vendor to ensure that adequate mixing is achieved for complete destruction of the combustion components of the process gases for all operating cases
44 | Text Box |  | Salman Jaffer | Per PID BRA-226708 sheet 1 of 1, the fuel gas is steam tracing is required
45 | Arrow |  | Salman Jaffer
46 | Line |  | Mohamed Ayyash
47 | Line |  | Mohamed Ayyash
48 | Text Box |  | Syed Ahmed | in order to reduce the vibration, Please consider to maintain a good space between the two combustion air blowers .
49 | Arrow |  | Syed Ahmed
50 | Callout |  | Mohamed Ayyash | add :
51 | Arrow |  | Mohamed Ayyash
52 | Line |  | Mohamed Ayyash
53 | Call-out |  | Ahmed Marhoon | Replace "BN-3500" with Bentley-Nevada BN-3500 or the latest"
54 | Call-out |  | Ahmed Marhoon | Add reference to all applicable BMPSs such as A3
55 | Call-out |  | Ahmed Marhoon | Advise the supplier that the above list represents the minimum requirements and needs to be confirmed /expanded, as required, meeting the API standard and Hazop/SIL recommendations.
56 | Text Box |  | Salman Jaffer | Alternate destination for sulphur pit ejectors discharge is Incinerator. Therefore, this shall be considered in design of the incinerator stack and refractory.
57 | Arrow |  | Salman Jaffer
58 | Callout |  | BD Mori | Refractory shall be designed for flue gas composition considering all the operating cases specified in the data sheet.
59 | Line |  | BD Mori
60 | Callout |  | BD Mori | Delete
61 | Callout |  | Mohamed Ayyash | space
62 | Callout |  | Mohamed Ayyash | space
63 | Callout |  | Mohamed Ayyash | , commissioning
64 | Callout |  | Mohamed Ayyash | , start up