## 000-S-GRD-70001-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 17 | 986131 | Effluent generated, and estimated solid waste generated during maintenance. method to safely dispose the solid waste.
2 | Call-out | 4 | A.Jabbar Mahmood | Add a space
3 | Callout | 7 | Adnan Alothman | For all critical equipment, company representative attendance is required as per BMPS-B11.
4 | Call-out | 16 | Ahmed Ali | add: , back washing, shutdown
5 | Text Box | 1 | Ahmed Marhoon | The following are comments related to instrumentation and control. 1. The package contains Air Blowers. Add a clear note on Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement. Requirement of MCM to be verified with the supplier. Reference to BMPS-J15 MCM to be added. 2. Instruct the supplier to source instrumentations from project AVL only. 3. Add a note to the supplier with reference to the applicable BMPS to design and supply the system according to the final PID. Functional design specifications covered in this document shall be firmed based on the approved PID. Vendors to be clearly notified on the necessity to include all the Hazop3/SIL recommendations and changes made Post-EPC-Development. 4. Suppliers to be notified on the possibility of considering wireless instruments for non-critical monitoring devices. Reference to BMPS-J10 Wireless to be added if applicable and meeting the criteria (under development) of wireless measurement. 5. All the machinery monitoring probes etc. shall be factory fitted by the vendor and not at site. 6.Narrative/flow charts/cause and effect shall be provided for any control or sequence logic. 7. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting …etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31. 8. In addition to BMPS-J6 and J2, all applicable BMPS from J class to be added for the supplier to comply with. e.g. J2, J3, J15 ... etc. All instruments and control systems to be designed according to BMPS specifications. 9. Supplier to be instructed to generate all instrument data sheets, hook ups ...etc. in project specs (according to Bapco standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 10. Vendor/TTSJV shall provide a list of deviation from BMPS specifications, in addition to the requisition specifications, for owner's review and approval.
6 | Call-out | 7 | Ahmed Marhoon | Client involvement to be added.
7 | Call-out | 7 | Ahmed Marhoon | What about Hazop/SIL/CHAZOP, IFAT and SAT?
8 | Call-out | 8 | Ahmed Marhoon | Clause 3.3.2. is emphasizing on the consideration of Chinese vendors for the LP materials. This may mislead the suppliers and/or create bias towards specific market with possible compromise in project AVL. In case the clause is retained; the following statement/condition shall be added as per the project agreement: "provided that the Vendor has been qualified for use on the SATORP project or a Saudi Aramco or Chevron project for a similar service and in a comparable facility to BMP. This is a typical comment for all MR where similar clause is stated.
9 | Call-out | 22 | Ahmed Marhoon | Contractor is requested to validate the models quoted for the instrumentation and ensure that the latest models are supplied for BMP in accordance to the projects specifications. To avoid supplying an obsolete and/or products at their obsolescence phase, vendors to be instructed to provide Products Life-Cycles/Road-maps. For example, model YTA310 for ESD Transmitter has recently announced obsolete and needs to be replaced with the latest model number. This is a general comment that need to be globally addressed by the contractor.
10 | Text Box | 3 | Bernard.Grace | It shall be the Contractor’s (and Supplier’s / Subcontractor’s) responsibility to bring all conflicts and deviations to the Owner’s attention in a timely manner and request a ruling interpretation or a resolution in writing. Refer to Project Specification No. BMPS-A2 (Specifications, Codes and Standards) for guidelines on how to manage conflicts and deviations.
11 | Call-out | 11 | Mahdi Ali | Add space
12 | Callout | 2 | Mohamed Ayyash | INDEX PAGE 2/25 ITEM 2: Typo, should read "OBJECTIVE" and not OBJECT.
13 | Callout | 3 | Mohamed Ayyash | PAGE 2/25 ITEM 2: Typo, should read "OBJECTIVE" and not OBJECT.
14 | Callout | 11 | Sankara | Correct as: Motors