## 010-E-DAT-00034-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 2 | alexis.martinez | API Standard 661, Seventh Edition - July 2013, restricts the face velocity to 700 ft/min for forced draft. Report the actual ft/min velocity and confirm that it meets the API requirement.
2 | Call-out | 3 | Mahdi Ali | Do not use FEED drawing number
3 | Text Box | 1 | 986131 | Fill in the Air-Cooler Heat exchanger checklist as given in API 661 and submit along with the data sheet.
4 | Callout | 1 | Mohamed Ayyash | General Comment: Fonts are too small throughout the data sheets and unreadable.
5 | Text Box | 3 | Ahmed Ali | General item for all air cooler data sheet, retain the note "Bundle to be self draining"
6 | Text Box | 3 | Ahmed Marhoon | Note 6: The scope for instrumentation and control is not limited to the alarms in DCS. All the control functions will be done in the DCS with the necessary interconnections with the electrical MCC. The final design of the system shall be based on the BMPS specifications (including relevant J class) and the final PID post detail design and Hazop3/SIL analysis. Suppliers to be instructed accordingly. This is a typical comment for all fin fan air coolers.
7 | Cloud+ | 3 | Mohamed Ayyash | Page 3/3 Notes 2 and 7 to be align for better representation inline with other notes.
8 | Cloud+ | 2 | Yousif Ahmadi | Per FEED data sheet outlet and inlets nozzles are 2 each. Check and confirm
9 | Call-out | 3 | 986131 | Please recheck the basis for the design duty as it does not match with heat and material balance sheet. Check if additional duty required is based on 50% BFW and 50% SWS water - refer to Hazop 2 Node 2 deviation 7. Based on the check rephrase note 2 accordingly.
10 | Call-out | 2 | 986131 | Please refer to the API 661 data sheet (page 2 of 2) and add all the required fields under Controls air side
11 | Callout | 1 | Mohamed Ayyash | Top of cover page: add Unit name 7CDU. Apply to all sheets.