## 019-E-DAT-00015-001
ID Nº | Subject | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Stamp | Raj |  |  | -
2 | Cloud+ | A.Jabbar Mahmood | Per BMPS A1, the CW design temperature is 165°F as also indicated in the FEED D/S. Review and confirm. | MOC Process: Design temperature increased to cover the scenario of tubes side blockage. RV1967 thermal relief temperature is 266ºF, and as per BMPS A3 section 7.2, 'The Design Temperature (minimum) should be the minimum expected temperature under operating and short-term conditions, including depressurization and relief valve operation.' | -
3 | Cloud+ | bapco-user | Tube side design temp. is 165 as per FEED data-sheet. EPC to verify. | See ID Nº 2 | -
4 | Call-out | Jawad Alawi | Add SA179 | Added | Y
5 | Cloud+ | Jawad Alawi | Seamless | Checked | Y