## 019-E-DAT-00046-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Typewritten Text | 1 | Mohamed Ayyash | Many text fonts throughout the document are too small and unreadable. Please enlarge
2 | Typewritten Text | 1 | Mohamed Ayyash | comment:
3 | Typewritten Text | 1 | Mohamed Ayyash | General
4 | Callout | 1 | Mohamed Ayyash | Typo, should read No.. to be applied to all sheets
5 | Callout | 1 | Mohamed Ayyash | Unit name missing. Add 2HCU, Apply to all sheets
6 | Callout | 1 | Mohamed Ayyash | Typo. delete c
7 | Call-out | 2 | A.Jabbar Mahmood | The inlet pressure is 168 psig as per FEED D/S. Owner cannot verify the updated inlet pressure without the updated hydraulic calculations.
8 | Callout | 2 | Mohamed Ayyash | Delete ";" in 3 locations marked with clouds (have no meaning)
9 | Call-out | 3 | A.Jabbar Mahmood | The inlet pressure is 168 psig as per FEED D/S. Owner cannot verify the updated inlet pressure without the updated hydraulic calculations.
10 | Cloud+ | 4 | A.Jabbar Mahmood | Correct the equipment number per the updated equipment numbering to 019P0020A/B/C
11 | Text Box | 4 | Hasan Asad | The Vendor/Supplier shall provide provision for extending the greasing ports to the platform level without the need of shutting down the fan and to reach the fan bearings ports for greasing. The Contractor shall include this requirement in the scope of supply for engineered solution.
12 | Text Box | 4 | Hasan Asad | The fans shall be equipped with anti-rotation mechanism.
13 | Callout | 4 | Yousif Ahmadi | Note 10 of data sheet to be added: Two fans per bay shall be provided as minimum.
14 | Call-out | 4 | Ahmed Marhoon | The scope for instrumentation and control is not limited to the alarms in DCS. All the control functions will be done in the DCS with the necessary interconnections with the electrical MCC. The final design of the system shall be based on the BMPS specifications (including relevant J class) and the final PID post detail design and Hazop3/SIL analysis. Suppliers to be instructed accordingly. This is a typical comment for all fin fan air coolers.
15 | Call-out | 4 | Mahdi Ali | Use Bapco number. FEED numbers shall not be used.