## 085-E-DAT-00002-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | Page 1 | Mohamed Ayyash | Delete BMP
2 | Callout | Page 1 | Mohamed Ayyash | Delete BMP
3 | Callout | Page 1 | Mohamed Ayyash | Water (add)
4 | Text Box | Page 1 | 986131 | The following Bid Clarification effect the Water circulation rate (refer row 1 of datasheet) T579,T703,T810,T1544 Please ensure these are considered while recalculating the water circulation rate. In addition vendor data for package units are also likely to impact the final flow rate based on detailed engineering work.
5 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
6 | Cloud+ | Page 2 | A.Jabbar Mahmood | It is 32178 gpm per FEED D/S. Check and confirm. Anyway, this number will need to be updated once the CW consumption in the user units has been finalized during EPC.
7 | Cloud+ | Page 2 | A.Jabbar Mahmood | 673 gpm per FEED D/S. Check and confirm
8 | Callout | Page 2 | Mohamed Ayyash | Kingdom of
9 | Callout | Page 2 | Mohamed Ayyash | Water (add)
10 | Callout | Page 2 | Mohamed Ayyash | Delete BMP
11 | Call-out | Page 2 | 986131 | Please re-check the evaporation loss (refer below caclulactions): Heat of water cooling = Mc Cp DT Wc=33118gpm Mc=7446251.12kg/hr(density as 61.8 lb/ft3) Cp=4.184 kJ / kg / °C DT=12deg C Heat=373861376.2KJ/hr Water evaporated = heat/ Hv HV2260 kJ / kg We=165425kg/hr =736gpm
12 | Callout | Page 2 | Julio.Aguilar | Basis for Water circulation and evaporation losses figures shown in this Mechanical Process Data Sheet shall to be matched with unit u085 Process Design Basis and PFDs.
13 | Text Box | Page 3 | Antony.Bentley | Add min. concrete grade & BMPS reference
14 | Callout | Page 3 | Mohamed Ayyash | Kingdom of
15 | Callout | Page 3 | Mohamed Ayyash | Water (add)
16 | Callout | Page 3 | Mohamed Ayyash | Delete BMP
17 | Callout | Page 4 | bapco-user | As per BMPS-E8 point 6.10.1
18 | Callout | Page 4 | Mohamed Ayyash | Delete BMP
19 | Callout | Page 4 | Mohamed Ayyash | Water (add)
20 | Callout | Page 4 | Mohamed Ayyash | Kingdom of
21 | Callout | Page 5 | bapco-user | Drive Shaft: Austen SS or Carbon fiber composite
22 | Callout | Page 5 | Mohamed Ayyash | Kingdom of
23 | Callout | Page 5 | Mohamed Ayyash | Water (add)
24 | Callout | Page 5 | Mohamed Ayyash | Delete BMP
25 | Callout | Page 5 | Mohamed Ayyash | add space
26 | Cloud+ | Page 6 | A.Jabbar Mahmood | Correct typo
27 | Cloud+ | Page 6 | A.Jabbar Mahmood | Typo
28 | Cloud+ | Page 6 | A.Jabbar Mahmood | 880 USGPM as per FEED H&MB Data. Check and confirm
29 | Callout | Page 6 | bapco-user | Note10: Typo error TDS: 184 ppm max
30 | Callout | Page 6 | Mohamed Ayyash | Water (add)
31 | Callout | Page 6 | Mohamed Ayyash | add space
32 | Callout | Page 6 | Mohamed Ayyash | Water (add)
33 | Callout | Page 6 | Mohamed Ayyash | Delete BMP
34 | Callout | Page 6 | Mohamed Ayyash | not standard, write full word
35 | Callout | Page 6 | Mohamed Ayyash | not standard, write full word
36 | Callout | Page 6 | Mohamed Ayyash | Water (add)
37 | Callout | Page 6 | Mohamed Ayyash | Water (add)
38 | Callout | Page 6 | Mohamed Ayyash | be (add)
39 | Call-out | Page 6 | 986131 | Reconfirm the number based on evaporation loss figures.
40 | Call-out | Page 6 | 986131 | For clarity of note 9 & 10 please capture the entire explanation given in 2520-u085-CN0007-01B, section 2.2.
41 | Call-out | Page 6 | 986131 | Reconfirm the number based on evaporation loss calculation, drift loss and blow down.
42 | Call-out | Page 6 | 986131 | Please include the contribution of TDS and chloride in the circulating water based on these chemical addition. In addition, provide contribution on TDS individually for each of the chemicals at the COC of design 7 and Normal 8.
43 | Text Box | Page 6 | Julio.Aguilar | Consider inclusion of a note saying:" Maximum allowed cooling water temperature from individual user at unit u085 inlet battery limit is 120 F."
44 | Callout | Page 6 | Julio.Aguilar | Please clarify Note 3 mentioning that that the wet bulb temp is 87F+1F
45 | Call-out | Page 6 | Ali Abbas | Refer to typical comments in 085-E-DAT-00001-001-RAP