## 085-S-DAT-00013-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Isamu | Content indicates specifications. Please consider rewording of this title. Applicable to all documents in this transmittal
2 | Call-out | 1 | MAK | COOLING WATER TOWER OR CWT for short form. This change shall be reflected globally.
3 | Text Box | 1 | MAK | The correct document template (cover page and format) shall be used. MOC shall coordinate with the Directorate for the correct template.
4 | Text Box | 1 | Raj | Owner has reviewed and commented on the MR package submitted on Contractors request to solicit quotations from vendors at the earliest. This MR stands reviewed with Status Code 3.
5 | Callout | 3 | Isamu | This is specification but the cover page title is data sheet. Please provide consistency between the title and the content.
6 | Call-out | 6 | Ahmed Marhoon | How will the local control be achieved? The current revision of PID does not indicate this requirement. Will a local hand switch be provided at the field? or the idea is to have a manual reset on the solenoid valves? Also, what are the safety measures that will be in place during the manual control/sequence mode? The control system design shall be capable of allowing this operation and ensure a Bumpless transfer design is in place.
7 | Cloud+ | 7 | A.Jabbar Mahmood | Clarify why two filters?
8 | Cloud+ | 7 | A.Jabbar Mahmood | As per the H&MB data, the normal flow rate is 29 USgpm. Check, confirm and update documents (PFD, P&IDs, etc) accordingly
9 | Call-out | 7 | 986131 | Add: per filter
10 | Callout | 7 | alexis.martinez | In the section 3.3, second and 11th point of process requirements list, add "see table 3.1 in section 3.4".
11 | Callout | 7 | alexis.martinez | In the section 3.3, 5th and 10th point of process requirements list, replace the symbol "@" by "at the"
12 | Callout | 7 | alexis.martinez | GENERAL: use in the entire document the word "Manufacturer" instead of "MFR". Correct the document accordingly.
13 | Text Box | 8 | Sankara | BMPS-P2
14 | Call-out | 8 | A.Jabbar Mahmood | Guarantees on the minimum time between filter reloads shall be provided.
15 | Call-out | 9 | Ebrahim | and General Design Rules for Electrical System, BMPS-P1
16 | Text Box | 9 | A.Jabbar Mahmood | General: Filters and Calcite beds are being used interchangeably for the same item. Consistency shall be applied
17 | Call-out | 10 | A.Jabbar Mahmood | and easy access for filter reloading.
18 | Call-out | 10 | Ahmed Marhoon | Mixing of electrical and instrument component/signals is against the BMPS standard. HV electrical equipment shall be completely segregated from the LV control equipment. Junction boxes dedicated for instrumentation shall be designed and supplied in compliance with the BMPS specifications. This bullet to be amended accordingly.
19 | Call-out | 10 | Ahmed Marhoon | Documents supplied by the supplier/contractor shall be developed based on the owner standard formats provided for the project. Simplified version is not acceptable.
20 | Call-out | 10 | Ahmed Marhoon | Should "interlock" be replaced with "sequence"?
21 | Call-out | 10 | 986131 | calcite bed maintenance procedure - Provide procedure of unloading and loading the calcite media. Method statement to safely dispose the discarded media to be provided in accordance with the local law.
22 | Call-out | 10 | 986131 | Effluent generated, Including any sold waste that may be generated during bed replacement.
23 | Callout | 10 | alexis.martinez | In page 10, section 4, add "maintenance manuals" on point 17th.
24 | Call-out | 10 | 986131 | Consider providing platform for safe and ease of bed replacement.
25 | Call-out | 11 | 986131 | Add: Note 3 (for consistency with section 3.3)
26 | Call-out | 12 | Ahmed Marhoon | The table included does not cover all the piping material classes requirements. For instance, the material class and thickness of impulse tubing is not mentioned. According to BMPS-J2/J6, SS316 is to be considered for the instrument impulse tubing. In addition to the table, a reference to the applicable BMPS standard to be added in order to capture all the specifications requirements. This is a typical comment for similar sections on all transmittals where only a portion of the BMPS specification is extracted and included in the materials specifications.
27 | Callout | 12 | Yousif Ahmadi | Piping classes to be checked and confirmed considering low pH
28 | Call-out | 13 | MAK | General Comment: Bapco's Document/Drawing numbers shall be used for all references.