## 085-S-DAT-00015-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | MAK | COOLING WATER TOWER OR CWT for short form. This change shall be reflected globally. | Noted. It will be implemented in next revision. | Y
2 | Text Box | 1 | MAK | The correct document template (cover page and format) shall be used. MOC shall coordinate with the Directorate for the correct template. | Cover page and format is under preparation by JV Directorate. It will be implemented later. | N
3 | Cloud+ | 5 | A.Jabbar Mahmood | Clarify the statement. | According to P&ID and FEED data sheet, backwash shall be initiated when the flowrate totalizer value is more than a specified value. | Y
4 | Cloud+ | 5 | A.Jabbar Mahmood | Clarify this statement. | According to P&ID and FEED data sheet, backwash shall be initiated when the flowrate totalizer value is more than a specified value. | Y
5 | Text Box | 6 | Mahdi Ali | Equipment tag is not as per BMPS-A8 | Basin tag has been changed to 085BA0003 | N
6 | Call-out | 6 | A.Jabbar Mahmood | As per the PFD, the basin is numbered as 085BA0002. Check and update | Correct tag is 085BA0003. PFD shall be updated. | N
7 | Call-out | 6 | Ahmed Marhoon | How will the local control be achieved? The current revision of PID does not indicate this requirement. Will a local hand switch be provided at the field? or the idea is to have a manual reset on the solenoid valves? Also, what are the safety measures that will be in place during the manual control/sequence mode? The control system design shall be capable of allowing this operation and ensure a Bumpless transfer design is in place. | Final control system description to be defined in a later stage, once technical offers are received. | N
8 | Cloud+ | 7 | A.Jabbar Mahmood | As per the H&MB data, the design flow rate is 4000 USgpm. Check, confirm and update documents (PFD, P&IDs, etc) accordingly | Capacity has been updated according to estimated utility information. To be confirmed once TTSJV has defined consumptions. H&MB and PFD will be updated accordingly | N
9 | Cloud+ | 7 | A.Jabbar Mahmood | Advise the basis of the max allowable pressure drop of 36 psi. | This maximum allowable pressured drop has been defined according to hydraulic calculation results performed by Process department. | Y
10 | Cloud+ | 7 | A.Jabbar Mahmood | As per the PFD, the pressure at the inlet of the flow control valve is 76 psig. Accordingly the pressure at the inlet of the filter is expected to be less than 76 psig. Check and update accordingly the appropriate documents. | Pressure has been revised and calculated hydraulically with current information. PFD will be updated accordingly. | N
11 | Call-out | 7 | 986131 | Add: "per filter" | Noted. It will be implemented in next revision. | Y
12 | Text Box | 8 | Sankara | P2 | MOC: Requirements regarding Ex protection are included also in BMPS-P2. BMPS-P3 is not applicable to this scope and is not included in 000-S-MRQ-70001-001. JV Directorate will check and include any additional specification as required | N
13 | Call-out | 8 | A.Jabbar Mahmood | The targetted TSS at the outlet of each filter shall be specified and guaranteed. | TSS required is 30 ppm normal / 35 ppm maximum. As indicated in Basis of Design. | N
14 | Cloud+ | 8 | 986131 | Review the TDS and Chloride based on the chemical dosing to the cooling tower and update. | This information has already been revised and updated according to the Basis of Design. | N
15 | Call-out | 8 | 986131 | Add in 3.5.: - Maximum pressure drop at normal water flow expected after backwash - Minimum operating time for the filter. - If the filter media is replaceable cartage then life of filter to be guaranteed. | Minimum operating time for the filter (21 hours) already required in design conditions. This is not a process guarantee indicated in Basis of Design Maximum pressure drop at normal water flow expected after backwash to be requested to Vendor and included in section 3.3 (Operating and Design conditions).Filter media is not replaceable cartridge | N
16 | Call-out | 9 | Ebrahim | and General Design Rules for Electrical System, BMPS-P1 | BMPS-P3 will be included instead of BMPS-P1. BMPS-P1 has not been included in 000-S-MRQ-70001-001 | N
17 | Text Box | 10 | Mahdi Ali | Layout | Noted. It will be implemented in next revision. | Y
18 | Call-out | 10 | Sameer Foujdar | Secondary cooling water side stream filters are three not eight. | Noted.It will be implemented in next revision. | Y
19 | Call-out | 10 | Ahmed Marhoon | Mixing of electrical and instrument component/signals is against the BMPS standard. HV electrical equipment shall be completely segregated from the LV control equipment. Junction boxes dedicated for instrumentation shall be designed and supplied in compliance with the BMPS specifications. This bullet to be amended accordingly. | Noted. It will be implemented in next revision. | Y
20 | Call-out | 10 | 986131 | access for removing and replacement of filter element / media. If a media is used then proper dump nozzles to be provided. | Scope indicated in Data Sheet is a general scope. This requirement will be added in MRQ. (000-S-GRD-70001-001).Nevertheless, following paragraph has been included: "...easy access for filter media replacement." in Manufacturer scope section. | Y
21 | Call-out | 10 | 986131 | Filter maintenance procedure - In case of cartage - provide replacement method. Method to dispose the cartage in accordance with the local environmental law to be provided. And if acid cleaning of other methods are to be employed provide the details. In case of media - provide procedure of unloading and loading the filter media. Method statement to safely dispose the media to be provided in accordance with the local law. Note: In case special cleaning procedure are to be employed (say acid cleaning etc.) adequate arrangement to be made to facilitate the same. | Noted. The following paragraph will be included: "MFR to provide procedure of unloading and loading the filter media". Any further instructions and requirements for correct operation and maintenance of package will be included in process philosophy and installation and operation manual. | Y
22 | Call-out | 10 | 986131 | Effluent generated, Including any sold waste that may be generated during bed/ cartage replacement. | MOC: Noted. The following wording will be included: "MFR to provide information regarding effluent generated in SIDE STREAM FILTERS , Including any sold waste that may be generated during according to 000-A-PRI-50004-001" | Y
23 | Call-out | 10 | 986131 | Consider providing platform for safe and ease of filter cartage/filter media replacement. | Scope indicated in Data Sheet is a general scope.For more detailed scope please refer to MRQ. (000-S-SOW-70001-001) The need of platform will be checked during tabulation stage once preliminary drawings are received. It is mentioned also in MRQ. (000-S-GRD-70001-001). | N
24 | Call-out | 13 | MAK | General Comment: Bapco's Document/Drawing numbers shall be used for all references. | New P&ID project numbers will be included when available. | N