## 310-F-DAT-00001-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout |  | BD Mori | Comments on this data sheet are also applicable to 311F001
2 | Callout |  | BD Mori | Vendor shall refer the relevant P&IDs for the specific notes applicable to this package
3 | Cloud+ |  | Julio.Aguilar | Remove AUXILIARY and replace for "No. 10 HP"
4 | Text Box |  | Jeung.Kim | This data sheet has to be updated according to FEED validation and detail design development such as finalized steam consumption.- typical comment for all data sheets.
5 | Callout |  | Mohamed Ayyash | No.
6 | Callout |  | Julio.Aguilar | Please, include new note number regarding steam sampling. See Sheet 7.
7 | Callout |  | BD Mori | TTSJV shall provide the basis for specifying 10% excess air for Boilers
8 | Callout |  | Julio.Aguilar | Add note if necessary to mention what standards were considered as basis of this figure.
9 | Callout |  | Julio.Aguilar | To be consistent throughout all document replace "Manufacturer" for "Supplier"
10 | Callout |  | BD Mori | For boiler design pressure margin, refer BMPS-F10 para 4.3
11 | Callout |  | BD Mori | Fuel Gas composition and operating conditions to be revised as per the latest revision in BMPS-A1
12 | Ellipse |  | Mohamed Ayyash
13 | Callout |  | Mohamed Ayyash | Don't center, better to use left justify
14 | Callout |  | BD Mori | TTSJV shall explain purpose of this note
15 | Callout |  | BD Mori | Add new note: Vendor shall guarantee the purity of the steam produced from the boiler as specified in as per BMPS-A1.
16 | Callout |  | Julio.Aguilar | Add note: Vendor shall provide stack sample line to ground for collection flue gas sampling by using portable analyzers.
17 | Cloud+ |  | Sameer.Ahmed | These analyzers are not included in the current MR scope of work as per this note, however, this is not mentioned in the exclusion section 3.2 of "Particular Technical Specification"
18 | Callout |  | Julio.Aguilar | Number of this note to be added in the sheet 2, row 28 for steam
19 | Callout |  | Julio.Aguilar | As per U372 unit Process Design Basis and PID BFW pressure to new HP boilers (No 10&11) is 875 psig from pump P3746. Unit u310 PFD shows 830 psig for the BFW from pump P3746. Final figure for the operation pressure going to new boilers to be confirmed to be consistent for all documents involved including this PDS.
20 | Arrow |  | Julio.Aguilar