## 311-F-DAT-00001-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ |  | Julio.Aguilar | Remove AUXILIARY and replace for "No. 10 HP"
2 | Callout |  | Mohamed Ayyash | No.
3 | Callout |  | Julio.Aguilar | Please, include new note number regarding steam sampling. See Sheet 7, 310F0001.
4 | Callout |  | Julio.Aguilar | Add note if necessary to mention what standards were considered as basis of this figure.
5 | Callout |  | Julio.Aguilar | To be consistent throughout all document replace "Manufacturer" for "Supplier"
6 | Callout |  | BD Mori | TTSJV shall provide the basis for specifying 10% excess air for Boilers
7 | Callout |  | BD Mori | For boiler design pressure margin, refer BMPS-F10 para 4.3
8 | Ellipse |  | Mohamed Ayyash
9 | Callout |  | Mohamed Ayyash | Don't center, better to use left justify
10 | Callout |  | BD Mori | Fuel Gas composition and operating conditions to be revised as per the latest revision in BMPS-A1
11 | Callout |  | Julio.Aguilar | As per U372 unit Process Design Basis and PID BFW pressure to new HP boilers (No 10&11) is 875 psig from pump P3746. Unit u311 PFD shows 830 psig for the BFW from pump P3746. Final figure for the operation pressure going to new boilers to be confirmed to be consistent for all documents involved including this PDS.
12 | Callout |  | Julio.Aguilar | Add note: Vendor shall provide stack sample line to ground for collection flue gas sampling by using portable analyzers.
13 | Callout |  | BD Mori | TTSJV shall explain purpose of this note
14 | Callout |  | BD Mori | Add new note: Vendor shall guarantee the purity of the steam produced from the boiler as specified in as per BMPS-A1.