## 382-A-BOD-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 12 | Julio.Aguilar | #3 API Separator
2 | Callout | 4 | Julio.Aguilar | (382BA0001B)
3 | Call-out | 6 | Hasan Al Noaimi | 1HRU
4 | Call-out | 6 | Hasan Al Noaimi | 50 persons
5 | Callout | 4 | Sameer.Ahmed | add: "except sanitary waste"
6 | Call-out | 3 | Mahdi Ali | Avoid using word 'New'.
7 | Cloud+ | 9 | Julio.Aguilar | Basis for selecting the sanitary water composition to be provided
8 | Cloud+ | 10 | Julio.Aguilar | Basis for selecting the sanitary water composition to be provided
9 | Call-out | 4 | Edgardo | change to "other"
10 | Text Box | 1 | Julio.Aguilar | Cover page to comply with the homogeneization procedure (000-A-PRO-50006-1) to be consistent with all OCs
11 | Call-out | 5 | MAK | CWT
12 | Call-out | 6 | Hasan Al Noaimi | CWT
13 | Call-out | 14 | Hasan Al Noaimi | CWT
14 | Callout | 12 | Julio.Aguilar | design.
15 | Callout | 8 | Salman Jaffer | Do you mean New Crude Oil Tanks - Water Draw-off?
16 | Text Box | 2 | Mahdi Ali | Equipment numbers in this document shall follow latest equipment list. All pumps to retain FEED tag numbers.
17 | Cloud+ | 5 | Julio.Aguilar | FEED document number to be updated
18 | Callout | 7 | Bernard.Grace | Flow in sewer lines shall run at 75% of the internal height of pipe, rising to a maximum of 93% in the event of firewater being added in accordance with BMPS-S1 Paragraph 10.1.3
19 | Call-out | 3 | MAK | General Comment: Always enter the whole equipment no. e.g., 382BA0006
20 | Callout | 4 | Sameer.Ahmed | How about the sanitary from the South Control Building?
21 | Callout | 21 | Sameer.Ahmed | How about the sanitary from the South Control Building?
22 | Callout | 3 | Bernard.Grace | Include information on the disposal of waste water from the laboratory
23 | Text Box | 6 | Sankara | Include Refinery South Control Building
24 | Call-out | 5 | Hasan Al Noaimi | N2 Plant
25 | Call-out | 6 | Hasan Al Noaimi | N2Plant
26 | Call-out | 6 | Hasan Al Noaimi | No 3Sulphur Plant
27 | Call-out | 5 | MAK | NO. 3
28 | Call-out | 5 | MAK | NO. 3
29 | Call-out | 4 | Edgardo | please change to "subsequent"
30 | Call-out | 4 | Edgardo | Please confirm how the sanitary sewage from the Maintenance Workshop will be handled
31 | Call-out | 19 | Edgardo | Please delete the prefix "f" in Unit 382. This comment applies whenever the prefix "f" is shown with the unit number
32 | Call-out | 15 | Edgardo | Please reconfirm the sanitary basin and pumps for the Maintenance Shop area; In Clause 4.9, Basin 382BA0003 is for Operation Building.
33 | Call-out | 5 | Hasan Al Noaimi | Refinery south flare
34 | Callout | 12 | Julio.Aguilar | remove prefix u
35 | Cloud+ | 7 | Julio.Aguilar | Replace "hypothesis reported in chapter 4" by " considerations mentioned on Section 4"
36 | Call-out | 3 | Edgardo | Replace the word "based" with the word "sufficient"
37 | Call-out | 3 | Edgardo | Replace this phrase with the word "excess"
38 | Call-out | 3 | Edgardo | replace with the word "for"
39 | Text Box | 21 | Julio.Aguilar | Sanitary waste water streams from Maintenance workshop to 382BA0002A,B,C and 382BA0003 are not shown here. Please confirm.
40 | Call-out | 3 | Edgardo | The reference document is the Scoping report prepared during Pre-FEED and may no longer be applicable now that the project is in EPC phase; It is suggested to delete this phrase
41 | Text Box | 1 | Sameer.Ahmed | This document is given CODE-2 as a special case to allow TTSJV to proceed with development of subsequence deliverables and procurement activities. However, TTSJV shall be responsible to incorporate the comments and complete the design before finalizing the equipment PO. BOD shall be modified to incorporate the updated streams data balance.
42 | Cloud+ | 18 | Sameer.Ahmed | This paragraph to be rewritten as follow: Two Final Sanitary Pumps are provided as spare due to (1) high maintenance frequency expected and (2) high criticality as the Final Sanitary Basin collects sanitary water from all the other lifting stations and no overflow to the sea is allowed.
43 | Callout | 12 | Sameer.Ahmed | Unit 085 is now called "Cooling Water Tower (CWT)". This shall be updated on all the document.
44 | Callout | 6 | Julio.Aguilar | Values for paved areas to be updated as per later Plot Plan
45 | Callout | 15 | Bernard.Grace | What about Refinery South Control Building (50 personnel)