## 098-A-BOD-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | Julio.Aguilar | No. 3, No. 4
2 | Cloud+ | 1 | Julio.Aguilar | Cover Page (Unit tittle/tag) to comply with the Homogenization procedure (000-A-PRO-50006-1) and standardization procedure to be consistent with all OCs for all Process Design Basis throughout the projects.
3 | Callout | 1 | balagangadhar.k | Match date format
4 | Callout | 2 | Julio.Aguilar | Section for Acronyms/Abbreviations to be included to be consistent with other OCs. Standardization to be considered.
5 | Text Box | 3 | Julio.Aguilar | Please check the acronyms/abbreviation throughout all the document and include them in the list in the new section to be created.
6 | Callout | 3 | BD Mori | Crude and Vacuum Distillation Units (7CDU/VDU)
7 | Callout | 3 | BD Mori | gas cooling section,
8 | Callout | 3 | BD Mori | Delete these references as the document numbers and revision will change
9 | Callout | 3 | BD Mori | of 1RHCU, 2HCU, 3HDU, 3/4TGTU
10 | Callout | 3 | balagangadhar.k | Paragraph spacing, check throughout document
11 | Callout | 3 | balagangadhar.k | Remove "s"
12 | Callout | 3 | balagangadhar.k | copy from section 1 of "2520-s036-CN-0009-01_B" document and use the same across all applicable deliverables for consistency
13 | Callout | 3 | balagangadhar.k | Clearly write "No.3 Hydrogen Plant (3H2P) & No.4 Hydrogen Plant (4H2P)" and use plant short description "3H2P & 4H2P" in rest of the document
14 | Callout | 3 | balagangadhar.k | BAPCO
15 | Callout | 4 | Syed Ahmed | Adsorption
16 | Callout | 4 | BD Mori | When will this information be available from Licensor? To be incorporated before this BOD is approved.
17 | Callout | 4 | BD Mori | Reword: Sweet Khuff Gas Feed from BAGRU
18 | Callout | 4 | BD Mori | Not consistent 3/4 Hydrogen Plant PFDs. Correct these values as per 3/4 Hydrogen Plant PFD. Indicate value for one pant and provide a note stating that the values provided for one plant, and applicable for both the plants.
19 | Callout | 4 | balagangadhar.k | reword to "Sweet Khuff Gas" all over the document
20 | Callout | 4 | balagangadhar.k | Composition for H2O & CO2, not matching with BAGRU HMB or PFD
21 | Callout | 4 | balagangadhar.k | Replace "," with "." for all values
22 | Callout | 4 | balagangadhar.k | Do not provide molar/mass rates to avoid confusion. only part of BAGRU sweet gas is used as H2P feed.
23 | Call-out | 5 | Hasan Al Noaimi | and operations flexibilty
24 | Cloud+ | 5 | Julio.Aguilar | Doc number to be updated.
25 | Callout | 5 | Syed Ahmed | Use word purge gas instead of tail gas (please refer to page 4 first paragraph)
26 | Callout | 5 | Syed Ahmed | Use word Sweet instead of treated as per (BMPS-A1)
27 | Callout | 5 | Salman Jaffer | revised
28 | Callout | 5 | BD Mori | Move this to top of the table
29 | Callout | 5 | BD Mori | Methane
30 | Callout | 5 | BD Mori | When will this information be available from Licensor? To be incorporated before this BOD is approved.
31 | Callout | 5 | BD Mori | Replace Syngas with Process Gas
32 | Callout | 5 | BD Mori | as fuel
33 | Callout | 5 | BD Mori | Supplementary fuel
34 | Callout | 5 | BD Mori | sweet
35 | Callout | 5 | BD Mori | er
36 | Callout | 5 | balagangadhar.k | Reword the note to "Refer 2&3BAGRU heat and mass balance (WP-PR-HMB-0001_Rev.1) for Sweet Khuff Gas characteristics."
37 | Callout | 5 | balagangadhar.k | of
38 | Call-out | 6 | Hasan Al Noaimi | No 1 Hydrogen Plant product purity is 94%. No 2 hydrogen plant H2 product purity 99.9% will be mixed with New but not with old one No 1.
39 | Callout | 6 | BD Mori | PSA purge
40 | Callout | 6 | BD Mori | are provided in H&M balance
41 | Callout | 6 | BD Mori | Delete reference to 1 H2 plant
42 | Call-out | 7 | Hasan Al Noaimi | No 3 Hydrogen Plant
43 | Call-out | 7 | Hasan Al Noaimi | No 4 Hydrogen Plant
44 | Call-out | 7 | Hasan Al Noaimi | No 1 H2 Plant goes to 2HDU H2 Header only.
45 | Call-out | 7 | Hasan Al Noaimi | write the name of the unit and delete new eg 1RHCU
46 | Call-out | 7 | Hasan Al Noaimi | 3HDU
47 | Call-out | 7 | Hasan Al Noaimi | 2HCU
48 | Callout | 7 | BD Mori | Why sweet off gas is shown here? If it is fuel gas , no need to show. Delete it.
49 | Callout | 7 | BD Mori | Indicate H2 supply to 1H2 P and delete incoming line from 1H2 P to the header
50 | Callout | 7 | BD Mori | Rename 1H2P
51 | Callout | 7 | BD Mori | Rename 2H2P
52 | Callout | 7 | BD Mori | Replace this with 1HCU, LBOU, 1TGTU
53 | Callout | 7 | BD Mori | Product
54 | Callout | 7 | BD Mori | Refer Licensor Process Guarantee Agreement (BRE-243580-h098/h099 page 2 of 6.) Methane impurity is not included in the product.
55 | Callout | 7 | Salman Jaffer | vppm
56 | Callout | 7 | BD Mori | Add in separate table guarantee value of : Product Condensate Ex HP Steam Striper Ammonia, 3 wppm max, Methanol 10 wppm expected.
57 | Callout | 8 | BD Mori | Add: 550 steam purity
58 | Callout | 8 | BD Mori | Additional details are provided in the Licensor Process Guarantee Agreement (BRE-243580-h098/h099)
59 | Callout | 8 | BD Mori | Provide full form of UHC
60 | Callout | 8 | BD Mori | As per Fuel Gas BOD 058-A-BOD-50001-001) page 20 the H2S content is specified as 150 ppm max. Please review the information and correct as required. Also refer the final revision of the BMPS-A1
61 | Callout | 8 | balagangadhar.k | Replace " ," with " . " for all values
62 | Cloud+ | 9 | Julio.Aguilar | 2&3BAGRU
63 | Cloud+ | 9 | Julio.Aguilar | Replace by "HP Sweet Khuff Gas"
64 | Callout | 9 | BD Mori | Move table description to top of the table
65 | Text Box | 11 | Hasan Al Noaimi | 1HRU
66 | Call-out | 11 | Hasan Al Noaimi | 1RHCU
67 | Call-out | 11 | Hasan Al Noaimi | 3HDU
68 | Call-out | 11 | Hasan Al Noaimi | 2HCU
69 | Call-out | 11 | Hasan Al Noaimi | TGTU
70 | Text Box | 11 | Julio.Aguilar | Hydrogen balance to be revised and figures to be confirmed. It is suggested to mention the basis used including the capacity of the units used in the balance
71 | Callout | 11 | Syed Ahmed | LBOU
72 | Callout | 11 | Syed Ahmed | 1) 1H2 plant don't supply to 2H2 plant header due to low purity and low pressure. 2) Delete off gas from Hydrogen balance because it is not related to Hydrogen management. 3) Generation and consumptions values to be verified and updated in the new sketch.
73 | Cloud+ | 11 | A.Jabbar Mahmood | As per the 2HCU H&MB the maximum expected H2 requirement (design case-SOR) is 125800 MSCFD. It is also suggested that a footnote is added indicating that the "licensor guaranteed" maximum H2 consumption is about 130500 MSCFD.
74 | Call-out | 11 | A.Jabbar Mahmood | A H2 recycle stream from 2HCU Make-up H2 compressors to the H2 plants of about 4 MSCFD (to be confirmed during EPC) to be indicated.
75 | Callout | 11 | BD Mori | Replace the existing sketch with new updated sketch
76 | Callout | 11 | Salman Jaffer | 4) Update hydrogen production and consumption balance based on the latest values
77 | Callout | 11 | Fatema Hashem | 1RHCU H&MB SHOWS HYDROGEN FLOW OF 120000MSCFD. CHECK AND UPDATE ACCORDINGLY.
78 | Call-out | 11 | Ali Kadhem | As per the 3HDU H&MB the maximum flow of hydrogen makeup is for the operating case-SOR: 23088 MSCFD. To be checked/updated.