## 000-A-PRO-70002-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 8 | A.Jabbar Mahmood | Chemical and catalysts purchase activities shall be included.
2 | Callout | 10 | Robert.Kawitzki | , Buildings
3 | Callout | 6 | Robert.Kawitzki | 30 and 60% 3D model reviews shall be shown
4 | Callout | 9 | Robert.Kawitzki | add comma
5 | Text Box | 13 | Sankara | Add: 1. Electrical Consumer Lists 2. Electrical Monitoring & Control System ( EMCS) Drawings
6 | Text Box | 10 | Mahdi Ali | All of the above shall be modelled using the S3D.
7 | Text Box | 10 | Mahdi Ali | All of the above shall be modelled using the S3D.
8 | Call-out | 8 | A.Jabbar Mahmood | Also include issuing the Hazop reports
9 | Text Box | 8 | Mahdi Ali | and BMPS-L series
10 | Callout | 17 | Sankara | and BMPS-P2
11 | Callout | 8 | Robert.Kawitzki | and finalized at the 30% model review
12 | Call-out | 7 | 986131 | and issue of hydraulic report
13 | Call-out | 7 | A.Jabbar Mahmood | and issue of relief load calculations
14 | Call-out | 7 | 986131 | And relief summary report for each unit.
15 | Call-out | 7 | A.Jabbar Mahmood | and Utility Flow Diagrams (UFDs)
16 | Call-out | 14 | Abdulaziz | appropriate word shall be used e.g design specification
17 | Text Box | 8 | Mahdi Ali | as per best practice and BMPS-A8 guidelines
18 | Call-out | 14 | Abdulaziz | Below activities to be considered as subsequent activities: *Review equipment ITPs. *Review PC&C procedures/activities. *Review start up procedures / activities. *Review FAT & SAT procedures and participate as required. *Review PM, repetitive maintenance and functional test procedures. *Review SPILL sheet, commissioning spares and 2 years spares. *Participate in HAZOP, SIL and Criticality studies.
19 | Callout | 5 | Harshad.K.Patel | Change Dates to English in this table
20 | Callout | 18 | Harshad.K.Patel | change Loas to Load
21 | Call-out | 8 | Mahdi Ali | Change SP3D to S3D across the whole document
22 | Callout | 18 | Sankara | Clarify what PSA is.
23 | Call-out | 18 | Ahmed Marhoon | Comment regarding following the BMPS-A8 is applicable for all the disciplines.
24 | Call-out | 5 | Abdulaziz | Description shal read 7CDU/7VDU
25 | Call-out | 10 | RASHED SHOWAITER | Design and allocate lay-down area for Bapco Departments and Contractors T&Is portacabins, and heavy equipment and vehicle parking.
26 | Call-out | 19 | 986131 | Equipment inspection after installation and coordination with vendor supervisions (like column internals etc.)
27 | Call-out | 20 | Ahmed Marhoon | Final system to be reflected on this plan. At this stage, a firm methodology to be followed.
28 | Cloud+ | 5 | Adnan Alothman | General: Many Contractual Engineering Milestones are not included in the below tables. Contractor to include all milestones as per EPC Level 3 project Schedule.
29 | Callout | 9 | Robert.Kawitzki | hazoped and IFC
30 | Call-out | 10 | Abdulaziz | Heavy equipments mobilization and demobilization, lifting and lay down area design shall be considered
31 | Callout | 8 | Robert.Kawitzki | in accordance with BMPS-A8
32 | Call-out | 14 | RASHED SHOWAITER | In addition to pressure vessels. The following bullets points need to be included: -Furnace -Exchangers -Lines and fittings (piping) -Rigging and lifting equipment
33 | Callout | 7 | alexis.martinez | In section 6.4.1 include PFD and UFD in "P&ID's development"
34 | Call-out | 16 | Raj | Include interface with Licensors for Review of critical licensor documents as noted in the Scope of Work document for each Work Package
35 | Call-out | 8 | 986131 | including start-up and shutdown procedure.
36 | Call-out | 15 | Mahdi Ali | Inconsistent use of Client and Company.
37 | Text Box | 8 | Robert.Kawitzki | lead designer
38 | Text Box | 15 | Mahdi Ali | Leads
39 | Text Box | 18 | Robert.Kawitzki | Model shall be as per BMPS-A8
40 | Call-out | 5 | Abdulaziz | Numbering not in sequence
41 | Callout | 8 | Robert.Kawitzki | One word
42 | Call-out | 20 | Ahmed Marhoon | p Requirements of pre-commissioning and commissioning devices/tools have not been covered e.g. Calibrators, Multimeters ...etc.
43 | Text Box | 17 | Mahdi Ali | P&IDs
44 | Cloud+ | 20 | Ahmed Marhoon | Participation schedule to be specific.
45 | Call-out | 9 | Mahdi Ali | PGAs and Isometrics shall follow BMPS-A8 guidelines and not a direct extraction from S3D
46 | Call-out | 9 | Mahdi Ali | Pipe supports to be modelled using the S3D Hanger and Support module
47 | Call-out | 18 | Ahmed Marhoon | Plan to clarify if there would be any direct communication between the OCs and Vendors or it is limited to the JVD.
48 | Text Box | 19 | Ahmed Marhoon | Plan to handle minor changes on construction documents that requires re-issue of a document to implement a hardware correction at site shall be detailed. A procedure needs to be developed describing how will the corrections at site, if any, will be managed. e.g. of a change is rewiring of terminations during loop checks/SAT requires an official revision to be issued by the design office to authorize the change.
49 | Callout | 9 | Robert.Kawitzki | Please expand what this means. Standard pipe support details will be issued by the directorate to be used by all oc's
50 | Call-out | 2 | MAK | Provide this information on all pages.
51 | Text Box | 13 | Mahdi Ali | Refer to the BMPS-A8 Annexure for documents and drawings generated using SPEL
52 | Text Box | 12 | Mahdi Ali | Refer to the BMPS-A8 Annexure for documents and drawings generated using SPI
53 | Call-out | 16 | Mahdi Ali | Remove letter 'D' from the unit number
54 | Call-out | 5 | Raj | Re-number 1.1 to 1.10
55 | Call-out | 5 | A.Jabbar Mahmood | RHCU is not relevant to MOC
56 | Text Box | 13 | Mahdi Ali | Single Line Diagrams
57 | Call-out | 7 | RASHED SHOWAITER | Size and Schedule
58 | Text Box | 17 | Robert.Kawitzki | SmartPlant 3D Model
59 | Call-out | 7 | 986131 | solid waste summary and disposal methods (example - Catalyst or disposable filter elements, etc.)
60 | Call-out | 6 | Abdulaziz | SS'S shall be defined in full form
61 | Text Box | 1 | mark.langerhorst | System Commissioning & Completions - Comments 6.3 Engineering Milestones There is no System Completions related milestones indicated. 1. Advise in case engineering data is ready for input into CMS. EasyPlant? 2. Tag numbering completion and interface with SC system and sub system numbering is an important point. 3. At what point are the System and Sub System limits/boundary drawings developed in conjunction with engineering. 6.5 Engineering Interfaces 6.5.1 Would there be no interface between Completions/Commissioning counterparts during the Engineering phase? 6.5.2.3 What about comments from SC, Operations and Commissioning who would review P&ID from systematic/operability point of view? Ignore comment if you think it is covered in Section 6.5.7. 6.5.2.4 Would it not be beneficial to have a systematic split facility in the Model as well as working areas? 6.5.7 A. SC,Pre Comm and Commissioning need to participate in key areas other than safety and operability matters During Engineering phase as previously mentioned. 1. Project tag numbering and System/Sub System numbering are aligned at the outset, identification of System and Sub system numbering and develop System and Sub system mark ups. 2. P&ID review 3.3 D Model review 4. HAZOP sessions 5. Constructability 6. Set up and population of the CMS in this case EasyPlant B. Should read Pre Commissioning and Commissioning. C. Is this referring to Pre Commissioning and Commissioning temporaries? If it is, very nonspecific. It should include items like temporary fabrications etc. D. Would it not be specified by SC/Commissioning? E. What about identification of specialist vendor services required? 1. Hot oil flushing 2. Chemical cleaning 3. Flange Management 4. Pipe cleaning ie. retrojet 5. Optalign 6. Preservation services. F. Consumables. G. Should read Pre Commissioning and Commissioning phase. 6.6 Do the Engineering Software Tools interface with CMS in this case Easy Plant? It is essential that Engineering data and especially changes are flagged up in the CMS.
62 | Call-out | 15 | A.Jabbar Mahmood | The Contractor shall ensure that technical queries are discussed with the client before being passed to the TSSJV and/or Licensors. The relevant client representatives in MOC shall be kept copied in the communication process.
63 | Call-out | 11 | Ahmed Marhoon | The list of activities related to the instrumentation and control discipline is incomplete. In case of deciding to list all the main activities in this document, the following activities are to be added: 1. Close coordination with the the client's representatives. 2. Participation in Hazop, SIL and Chazop studies. 3. Participation in IFAT, SAT, pre-commissioning and commissioning activities. 4. Participation in 3D model review sessions. 5. Participation in milestone sessions/meetings of the packages with suppliers. 6. Generation of all documents listed in the final project CDRL but not listed in this section such as Alarm and Test Procedures and SPILs. 7. Coordination with the other discipline leads, such as electrical and civil, to ensure all the instrumentation and control requirements are incorporated on the non-J class deliverables. 8. Assurance of compliance with the BMPS-J and General BMPS specifications in the design of the instrumentation and control systems. 9. Coordination with the TTSJV for the necessary standardization homogenization and harmonization across all OCs. 10. Manage and Issue of As-built documents related to instrumentation and control.
64 | Call-out | 5 | 986131 | The milestones with respect to SGP, Cooling towers, Tank farm/BFW/Condensate missing in the list. For 7CDU/VDU not all milestones are shown.
65 | Text Box | 11 | Mahdi Ali | The scope of the 3D modelling shall be followed for instruments, fire fighting systems, etc.
66 | Cloud+ | 17 | Ahmed Marhoon | The statement "normal flow of information" does not describe the actual responsibility and workflow for the instrumentation discipline. This process to be detailed to reflect the actual involvement.
67 | Call-out | 20 | Mahdi Ali | This document is not yet reviewed by Bapco. This document shall be read in conjunction with BMPS-A8
68 | Callout | 1 | Bernard.Grace | This document should be included within the JV Engineering Management Plan with pertinent points raised and the overall process if differnet frfom JV attached as an Annex. Otherwise there will be 4 reviews per document MOC, ROC, SOC & JV
69 | Callout | 9 | Bernard.Grace | This is not Civil, it is mechanical
70 | Call-out | 9 | Abdulaziz | To be replaced with crosschecked as possible
71 | Call-out | 6 | Mahdi Ali | Use Capital letters for the document number
72 | Text Box | 1 | MAK | Use the latest document template which is part of the Homogenization Procedure. MOC shall coordinate with JV Directorate.
73 | Call-out | 5 | A.Jabbar Mahmood | We assume this is as per the EPC Contract and hence not subject to change
74 | Callout | 10 | Bernard.Grace | What about foundations and superstructure design of Buildings (Substations etc)
75 | Call-out | 18 | 986131 | What about HSE reports - like dispersion models, noise contours etc.
76 | Call-out | 5 | Abdulaziz | WP3 is not relevant to MOC