## 044-E-DAT-00005-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
2 | Callout | Page 1 | Salman Jaffer | add unit name
3 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
4 | Cloud+ | Page 2 | Sameer.Ahmed | As per BMPS-A1 8.2.3, the standard lengths are 16ft, 30ft & 42ft
5 | Callout | Page 2 | balagangadhar.k | Refer FEED datasheet 2520-s044-SP-0810-07_C for 60# Blowdown Drum and cross check the operating temperature and pressure, change if required.
6 | Callout | Page 2 | BD Mori | Add reference to note 7
7 | Callout | Page 3 | Salman Jaffer | c) Type 'B' manifold. d) The degree of the slop for free draining purpose to be identified.
8 | Callout | Page 3 | Julio.Aguilar | add: according to BMPS-A3