## 047-E-DAT-00002-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC | Will be incorporated into PO Material Requisition, after revising the equipment numbering officially. | N
2 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs | All have been implemented, but will be updated at PO requisition as per the Homogenization Procedure (000-A-PRO-50006-1) revision. | Y
3 | Cloud+ | Page 2 | Sameer.Ahmed | This length is not as per BMPS-A1 8.2.3 | As per BMPS-A1 and BMPS-E7, preferred tube length is 16, 30, 42 ft. However, this limitation can be discussed during the EPC stage, as per Bid Clarification T883 for the economical reasons. It can be deeply discussed after TBE. | N
4 | Callout | Page 3 | Salman Jaffer | a) Please refer to Bid Query T1383 for the requirement for automatic louver b) Type 'B' manifold. c) The degree of the slop for free draining purpose per PIDs | a) Automatic louver has been applied at datasheet for air coolers of Sulphur Block as per T1383. b) Will be clarified at TBE stage c) Will be clarified at TBE stage | N
5 | Callout | Page 3 | Julio.Aguilar | add: according to BMPS-A3 | Minimum design temperature has been called many BMP specifications, especially BMPS-E7. No need to specify BMP-A3. | N
6 | Callout | Page 3 | BD Mori | To be consistent with FEED data sheet add note : 047E4712 shall be identical to 046E4612. | Comment incorporated. | Y