## 048-E-DAT-00003-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC
2 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs
3 | Callout | Page 1 | BD Mori | LP
4 | Cloud+ | Page 2 | Sameer.Ahmed | As per BMPS-A1 8.2.3, O.D. 25.4 (1)
5 | Cloud+ | Page 2 | Sameer.Ahmed | Add note: Length to be as per BMPS-A1 8.2.3
6 | Callout | Page 2 | balagangadhar.k | Steam inlet to the air cooler is from a vessel operating at atmospheric pressure. Inlet Steam temperature shall be saturation temperature at vessel operating pressure which is 212 F. Please change the duty, inlet temperature, properties and flow rate. Flow rate should be higher than this due to flashing of additional condensate into steam.
7 | Callout | Page 3 | Salman Jaffer | Type 'B' manifold.
8 | Callout | Page 3 | Syed Ahmed | LP
9 | Callout | Page 3 | Julio.Aguilar | add: according to BMPS-A3