## 085-G-DAT-00002-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Isamu | Delete.
2 | Text Box | 1 | Mahdi Ali | remove space between sequence number and suffix
3 | Callout | 1 | Mohamed Ayyash | No. (Typo) apply to all document
4 | Text Box | 1 | A.Jabbar Mahmood | General: Decimal points shall be instead of commas as decimal separators
5 | Text Box | 1 | A.Jabbar Mahmood | General: The reported pump capacities and normal CW flowrates are not consistent with the design basis document, recently issued H&MB nor with the CWT datasheets. It is aslo understood that these numbers will be frozen at a later stage in the EPC once the CW consumptions for the users are finalized.
6 | Callout | 2 | Isamu | Please make clear if in parallel with main cooling water pumps as this in conflict with other notes. see comment on note 4 on page 19
7 | Cloud+ | 2 | A.Jabbar Mahmood | Ensure that the reported data, in particular and operating pressures, are consistent with BMPS A1
8 | Call-out | 2 | 986131 | Add: (note 31)
9 | Cloud+ | 2 | Adnan Alothman | Operating Conditions parameters are different than FEED DS. Verify & confirm
10 | Cloud+ | 2 | 986131 | data changed from FEED - Detail engineering work explaining the change to be submitted for Owner's review.
11 | Call-out | 2 | 986131 | Provide the NPSHa considering that the water is saturated with dissolved air. The revised NPSHa is expected to be low (liquid head above the pump suction minus the friction loss). To avoid a over conservative pump design indicate the Effective NPSHa, calculated at the pump suction pressure when the volume of the flashed gas is 2% (or lower figure if the dissolved gas is less) the total volume. Cover this through notes - as a example extract from a existing refinery pump is attached for your reference.
12 | Text Box | 4 | Hasan Asad | Shall be 3
13 | Call-out | 4 | Ahmed Ali | use the correct pump number 085P0002A/B
14 | Callout | 4 | Adnan Alothman | Seal supp. sys. mounted on Pump Baseplate to be checked and confirm against relative standard.
15 | Text Box | 5 | Hasan Asad | YES
16 | Text Box | 5 | Hasan Asad | WIT
17 | Text Box | 6 | Ahmed Marhoon | The following are general comments related to instrumentation and control: 1. The notes related to Instrumentation & Control provided on the Data Sheet do not capture all the technical requirements for the instruments design. All applicable BMPS-J series to be referenced (such as J2, J3, J18 &etc) for the supplier to comply with. 2. TTSJV is requested to ensure that all the specific technical/functional requirements (including AVL) are covered and detailed in the requisition specification that will be sent out to suppliers. In case this document would be the only one for MR, then all the relevant BMPS to be included in the Data Sheet notes. 3. Vendors to be notified on the fact that the final design of the system shall include all the Hazop3/SIL recommendations and approved PID post-EPC-development. 4. Since the Data Sheet is issued separately, the consistency between the different documents, that may be part of the requisition, could not be verified and hence it is the contractors responsibility to update the other documents impacted by any of the comments on this Data Sheet and vice versa. 5. Minimum Flow arrangement/design shall be reviewed and confirmed by the supplier. 6. Supplier to be notified on the requirements of the sequence operation, trip, autostart, permissive and other functional specification covered on the PID. 7. Add Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement. 8. Requirement of MCM to be verified with the supplier. Reference to BMPS-J15 MCM to be added accordingly. 9. Suppliers to be notified on the possibility of considering wireless instruments for non-critical monitoring devices. Reference to BMPS-J10 Wireless to be added if applicable and meeting the criteria (under development) of wireless measurement. 10. All the machinery monitoring probes etc. shall be factory fitted by the vendor and not at site. 11. Narrative/flow charts/cause and effect shall be provided for any control or sequence logic. 12. Assistance and involvement of the vendor during CHAZOP/Hazop workshops and study to be considered. 13. Explanatory notes to be added on the requirement of having the control performed in the plant DCS and safety functions in ESD system. 14. Scope of supply for the interposing relays to be clearly defined. 15. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 16. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting &etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31.
18 | Text Box | 7 | Sankara | Delete Ex p
19 | Call-out | 7 | Mahdi Ali | remove 'u' from unit number
20 | Callout | 7 | Mohamed Ayyash | Make space
21 | Cloud+ | 7 | Yousif Ahmadi | Change to: SECONDARY COOLING WATER CIRCULATING PUMPS ELECTRIC MOTOR
22 | Cloud+ | 7 | Yousif Ahmadi | Change to: 085P0002B and remove 085P0002 A/B
23 | Callout | 8 | Mohamed Ayyash | Make space
24 | Callout | 8 | Mohamed Ayyash | Align
25 | Cloud+ | 8 | Yousif Ahmadi | Change to: 085P0002B and remove 085P0002 A/B
26 | Cloud+ | 8 | 986131 | Ensure that all notes in this data sheet have a unique number to avoid confusion.
27 | Callout | 9 | Mohamed Ayyash | Delete u
28 | Callout | 9 | Mohamed Ayyash | Add :
29 | Callout | 9 | Mohamed Ayyash | Why write outside the table ?
30 | Callout | 9 | Mohamed Ayyash | Correct
31 | Cloud+ | 9 | 986131 | Ensure all note in this drawing has a unique number. Example note 1,2 & 4 on page 19 has no relavence to these notes.
32 | Callout | 12 | Mohamed Ayyash | increase font
33 | Text Box | 13 | Hasan Asad | Pump vendor shall provide LCCA for 20 years.
34 | Text Box | 17 | Hasan Asad | Yes
35 | Text Box | 17 | Hasan Asad | Include mechanical and electronic.
36 | Call-out | 18 | 986131 | These note have same number as notes in page 19. provide unique number for all notes in this data sheet.
37 | Callout | 19 | Isamu | See comment on page 2 and correct accordingly
38 | Call-out | 19 | Mahdi Ali | Use Bapco number
39 | Text Box | 19 | Hasan Asad | The owner standardized on John Crane with reliability and service repair contract. The API plan shall be accessible with filling cart for the seal pot.
40 | Call-out | 19 | A.Jabbar Mahmood | Ensure that this is inline with BMPS A1
41 | Text Box | 19 | 986131 | 31 The source of Cooling water is direct contact cooling tower and the water is saturated with air: Composition: Water: xx mole%, Air: yy mole%. (Contractor to fill the mole composition of water and air)
42 | Call-out | 19 | 986131 | NPSH test is required and not conditional. if additional NPSH test for lower than 1m - like API clause 8.3.4.3.3 or 8.3.3.6 - is required - then clearly specify.