## 098-E-DAT-00001-001-RAP-CS1
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | Page 1 | Mahdi Ali | Equipment numbers to follow final EPC equipment numbering which is under review by Bapco team in SOC | Will be incorporated into PO Material Requisition, after revising the equipment numbering officially. | N
2 | Text Box | Page 1 | Julio.Aguilar | Cover Page to comply with the Homogenization Procedure (000-A-PRO-50006-1) to be consistent with all OCs | All have been implemented, but will be updated at PO requisition as per the Homogenization Procedure (000-A-PRO-50006-1) revision. | Y
3 | Callout | Page 2 | Syed Ahmed | ,9 | Comment incorporated. | Y
4 | Cloud+ | Page 2 | Sameer.Ahmed | As per BMPS-A1 8.2.3, O.D. 25.4 (1) | Tube OD can be used from 1 inch to 1.5 inch, as per BMPS-E7 para. F.2.4.2, and will be defined during TBE. | N
5 | Cloud+ | Page 2 | Sameer.Ahmed | Add note: Length to be as per BMPS-A1 8.2.3 | As per BMPS-A1 and BMPS-E7, preferred tube length is 16, 30, 42 ft. However, this limitation can be discussed during the EPC stage, as per Bid Clarification T883 for the economical reasons. It can be deeply discussed after TBE. | N
6 | Callout | Page 3 | balagangadhar.k | Provide heat curves data at 3 different pressures for better accuracy. The data provided above does not fit into HTRI as it is. | Will be clarified with vendor during TBE. | N
7 | Callout | Page 3 | Salman Jaffer | Please refer to BMPS A-50003 for manifold requirement for air cooled items | Will be clarified with vendor during TBE. | N
8 | Callout | Page 3 | Salman Jaffer | Supplyer | Comment incorporated. | Y
9 | Callout | Page 3 | Julio.Aguilar | add: according to BMPS-A3 | Minimum design temperature has been called many BMP specifications, especially BMPS-E7. No need to specify BMP-A3. | N
10 | Callout | Page 3 | BD Mori | Based on the highest temperature, if required the vendor shall perform FEA analysis. | Will be clarified with vendor during TBE. | N