## 372-G-DAT-57002-001-RAP
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | Page 1 | Khalid | 372P3731 A/B/C
2 | Callout | Page 1 | Mohamed Ayyash | Typo, Should read No. (apply to all sheets.
3 | Typewritten Text | Page 1 | Mohamed Ayyash | General comment: Correct pumps numbers from 372P0031A/B/C to 372P3731A/B/C in all document
4 | Cloud+ | Page 1 | Mohamed Ayyash | Typo, delete "u" from unit number, should read 372
5 | Call-out | Page 1 | Mahdi Ali | Incorrect sequence number
6 | Call-out | Page 1 | Mahdi Ali | No spaces between the number and the suffix
7 | Text Box | Page 1 | A.Jabbar Mahmood | The pumps head and capacity are preliminary and will be finalized later during the detailed design when the CW requirement has been frozen. A note shall be added in this regard.
8 | Text Box | Page 1 | MAK | Use the latest cover page template that is part of the Homogenization Procedure. MOC shall coordinate with JV Directorate.
9 | Callout | Page 2 | Mohamed Ayyash | Page number should read 2/9. apply to all sheets
10 | Call-out | Page 2 | Sameer Foujdar | Cooling water inlet and return pressure to be inline with BMPS A1 for all the pumps data sheet in this transmittal 372 P37321, 372P3730, 050P0037, 019P0006, 019P0010.
11 | Text Box | Page 2 | Mahdi Ali | Check Equipment number
12 | Call-out | Page 2 | Mahdi Ali | Remove 'u' from the unit number
13 | Cloud+ | Page 2 | Adnan Alothman | Figures in OPERATING CONDITIONS table need to be checked against FEED data sheet and confirm.
14 | Callout | Page 4 | Adnan Alothman | Mounting of Seal Support System on Baseplate to be checked against relative standard and confirm.
15 | Text Box | Page 7 | Sankara | HV motors in Zone 2 areas shall be Ex-d or Ex-e type only. Refer Query T107: Typical Comment
16 | Callout | Page 7 | Mohamed Ayyash | Numbers from 1 - 117 to be centered inside cells (Pages 7 and 8)
17 | Call-out | Page 7 | Sameer Foujdar | 372M0031 A/B/C each require an individual motor and hence the number of units required should read as 3.
18 | Callout | Page 9 | Isamu | Delete. NPSHR test already specified as witness
19 | Cloud+ | Page 9 | Mohamed Ayyash | Overlap. There is a hidden text please correct
20 | Call-out | Page 9 | Mahdi Ali | Use Bapco number. FEED number shall not be used.
21 | Call-out | Page 9 | A.Jabbar Mahmood | Also add the basis for the having three pumps.