## 010-G-DAT-00009-001-RA-CS
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | MAK | Use the latest document cover page and API datasheet template which is part of the Homogenization Procedure. MOC Contractor shall coordinate with JV Directorate.
2 | Call-out | 2 | Abdulaziz | Standard edition to be included as applicable
3 | Call-out | 2 | 986131 | Please check the NPSH a for this case. NPSHa would be very low.
4 | Callout | 2 | alexis.martinez | Page 2, row 32, 33. Inconsistency of max. ambient temperature and relative humidity shown in page 2 and 7. Review and correct
5 | Callout | 2 | alexis.martinez | Page 2. Inconsistency in discharge, suction pressure, NPSHA and hydraulic power with FEED data sheet. Review and correct. The hydraulic calculation are required.
6 | Cloud+ | 2 | Mohamed Ayyash | Avoid text overlap wih table lines.
7 | Callout | 2 | Isamu | Delete from all sheets
8 | Cloud+ | 2 | Mohamed Ayyash | Use page no. 2/9 and not 2. Apply this to all pages
9 | Call-out | 3 | Abdulaziz | TR to clarify on the requirement of hydraualic fit coupling
10 | Call-out | 3 | Abdulaziz | TR to clarify on the requirement of non grouted construction
11 | Cloud+ | 3 | Mohamed Ayyash | Hidden text
12 | Call-out | 4 | Abdulaziz | To ensure easy and safe accessibility for the pump during regular and major maintenance.
13 | Cloud+ | 5 | Mohamed Ayyash | Avoid text overlap wih table lines.
14 | Text Box | 6 | Ahmed Marhoon | The following are general comments related to instrumentation and control: 1. The notes related to Instrumentation & Control provided on the Data Sheet do not capture all the technical requirements for the instruments design. In the RFI, all applicable BMPS-J series to be referenced (such as J2, J3 â€¦etc) for the supplier to comply with. 2. TTSJV is requested to ensure that all the specific technical/functional requirements (including AVL) are covered and detailed in the requisition specification that will be sent out to suppliers. In case this document would be the only one for MR, then all the relevant BMPS to be included in the Data Sheet notes. 3. Vendors to be notified on the fact that the final design of the system shall include all the Hazop3/SIL recommendations and approved PID post-EPC-development. 4. Since the Data Sheet is issued separately, the consistency between the different documents, that may be part of the requisition, could not be verified and hence it is the contractorâ€™s responsibility to update the other documents impacted by any of the comments on this Data Sheet and vice versa. 5. Minimum Flow arrangement/design shall be finalized in consultation with the supplier. 6. Add Design Philosophy BMPS-A3 reference section 8.5 MCM Guidelines. Monitoring system in general to meet the requirement stated in this BMPS in addition to vendor requirement. 7. Requirement of MCM to be verified with the supplier. Reference to BMPS-J15 MCM to be added accordingly. 8. Suppliers to be notified on the possibility of considering wireless instruments for non-critical monitoring devices. Reference to BMPS-J10 Wireless to be added if applicable and meeting the criteria (under development) of wireless measurement. 9. If applicable, all the BN machinery monitoring probes etc. shall be factory fitted by the vendor and not at site. 10. Narrative/flow charts/cause and effect shall be provided in clientâ€™s standard format for any control or sequence logic. 11. Assistance and involvement of the vendor during CHAZOP/Hazop workshops and study to be considered. 12. Explanatory notes to be added on the requirement of having the control performed in the plant DCS and safety functions in ESD system. 13. Scope of supply for the interposing relays to be clearly defined. 14. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 15. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting â€¦etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31. 16. Vendor/TTSJV shall provide a list of deviation from BMPS specifications, in addition to the requisition specifications, for owner's review and approval.
15 | Call-out | 7 | Ahmed Ali | desalter water
16 | Callout | 7 | Sankara | On line and not one line partial discharge couplers
17 | Call-out | 7 | Ahmed Ali | Desalter water
18 | Cloud+ | 7 | Mohamed Ayyash | Overlap, make a space in between
19 | Cloud+ | 7 | Mohamed Ayyash | Should read Motor
20 | Cloud+ | 8 | Mohamed Ayyash | Overlap, make a space in between
21 | Cloud+ | 8 | Mohamed Ayyash | Numbers not in sequence
22 | Text Box | 9 | Isamu | These improper technical wordings are confusing and should be deleted as you already referred the Vendor to BMPS which suffices,
23 | Text Box | 9 | Abdulaziz | M/SEAL vendor to be provided with operating parameter during, start-up/shutdown mode, study state condition an upset in order to provide the optimum design selection.
24 | Text Box | 9 | Isamu | Pump is not designed yet and the world design shall be used by Vendor only as per API definition. You may revise to indicate " 10% margin has been added to the rated flow.
25 | Text Box | 9 | Abdulaziz | M/SEAL vendor to be provided with operating parameter during, start-up/shutdown mode, study state condition an upset in order to provide the optimum design selection.