## 010-L-PPN-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | Mahdi Ali | 000-A-PPN-60001-001
2 | Text Box | 1 | Ahmed Marhoon | 1. Contractor to ensure that underground cable trench size and design is adequate to accommodate all the underground multipair cables with the necessary segregation from high voltage electrical trenches and 30% spare space for future use as per the BMPS-J series. Any deviation from this requirement shall be brought to owner's attention for review/evaluation. 2. Analyzers if not installed in ventilated analyzer house, shall be installed in field shelters. Contractor to consider space for these analyzers with the necessary access in the plot plan. In addition to the analyzers designed to be in analyzer house, there are other analyzers in the plant that need to be installed under shades.
3 | Text Box | 1 | Ahmed Ali | 2 maintenance access has been provided to the exchangers area which is improvement to the FEED plot plat, however TR to ensure that all the exchangers are included in the plot plan. Number of exchangers reduced from 21 in the feed to 18 in this plot plan
4 | Text Box | 1 | Ahmed Ali | A covered shelter (at least 5m x 10m in area) each for lube oil and for chemical storage shall be provided at each plant or train. The shelter shall have a raised concrete paving and with provision for spill containment and coated and protected with an approved material to prevent any penetration of chemical (in case of spillage) through the concrete and into the ground. The provision of sewer system for chemical and oil storage area shall be finalized during detailed design by EPC contractor and to Owner’s approval. The storage area should be close to the road for easy acces
5 | Text Box | 1 | Mohamed Aldoseri | Access stairs to be corrected
6 | Call-out | 1 | Hasan Al Noaimi | Add lube oil area on the plot and to be in shelter.
7 | Callout | 1 | Robert.Kawitzki | Align access road with clearway between building loading platform and back of pumps
8 | Callout | 1 | Robert.Kawitzki | All elevations to be noted with three digits after decimal point - typ comment
9 | Callout | 1 | Robert.Kawitzki | All pumps are inaccessible
10 | Callout | 1 | Erwin.Lugue | Allow structure to have removable roof panels for maintenance
11 | Text Box | 1 | Robert.Kawitzki | Are no auto ignition pieces of equipment placed downwind of heaters?
12 | Callout | 1 | Robert.Kawitzki | Are these filters? Confirm adequate maintenance access
13 | Call-out | 1 | MAK | Change L to A which is the correct Material Class for Plot Plan.
14 | Callout | 1 | Robert.Kawitzki | Clarify proposed electrical power supply and piping routing
15 | Callout | 1 | Robert.Kawitzki | Confirm accessibility to pumps and piping under structure - typ comment
16 | Callout | 1 | Robert.Kawitzki | Confirm adequate access is provided between pump/motor and console and piping - typ comment all pumps with LOCs
17 | Callout | 1 | Robert.Kawitzki | Confirm clearance for breakout spool removal - typ comment
18 | Callout | 1 | Fernando.Perez | Confirm Distance between the two line of pumps is suficient
19 | Callout | 1 | Robert.Kawitzki | Confirm sufficient maintenance and access clearance for equipment inside structures including associated piping - typ comment
20 | Callout | 1 | Robert.Kawitzki | Confirm that all main staircases are 1200mm wide - typ comment
21 | Callout | 1 | Robert.Kawitzki | Confirm that area is paved - typ comment for exchanger bundle access areas
22 | Callout | 1 | Robert.Kawitzki | Confirm why pumps are this far away from NS rack
23 | Callout | 1 | Erwin.Lugue | corresponds
24 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING
25 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING
26 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING
27 | Callout | 1 | Robert.Kawitzki | Crane parking area will block access to under rack during shutdowns
28 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING AT THESE LOCATIONS
29 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING AT THESE LOCATIONS FOR THE above EXCHANGERS
30 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING AT THESE LOCATIONS, AND TR TO ENSURE THE CRANE BOOM WILL REACH THE FIN FANS BUNDLES
31 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING AT THESE LOCATIONS, AND TR TO ENSURE THE CRANE BOOM WILL REACH THE FIN FANS BUNDLES
32 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING AT THESE LOCATIONS, AND TR TO ENSURE THE CRANE BOOM WILL REACH THE FIN FANS BUNDLES
33 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING AT THESE LOCATIONS, AND TR TO ENSURE THE CRANE BOOM WILL REACH THE FIN FANS BUNDLES
34 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING COO1 OVERHEAD AND RV
35 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING FOR COOLING TOWER T&IS
36 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING FOR COOLING TOWER T&IS
37 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING FOR COOLING TOWER T&IS
38 | Text Box | 1 | RASHED SHOWAITER | CRANE PARKING FOR STRUCTURED PACKING UNLOADING AND LOADING
39 | Callout | 1 | Erwin.Lugue | Curb? h=?
40 | Call-out | 1 | MAK | Delete P and never use prefixes for Unit Nos.
41 | Call-out | 1 | MAK | Delete. This is for Bapco use.
42 | Callout | 1 | Robert.Kawitzki | Delete?
43 | Callout | 1 | Robert.Kawitzki | Discharge lines to align for all 4 pumps refer BMPS A4 8.1.3
44 | Callout | 1 | Erwin.Lugue | Emergency exits & egress requirements to conform as per BMPS A5
45 | Callout | 1 | Robert.Kawitzki | Ensure access is adequate in regards to piping, supports and instruments - typ all round
46 | Cloud+ | 1 | Mohamed Ayyash | Equipment numbers overlapping correct
47 | Cloud+ | 1 | Mohamed Ayyash | Equipment numbers overlapping correct
48 | Cloud+ | 1 | Mohamed Ayyash | Equipment numbers overlapping move up slightly, space available
49 | Callout | 1 | Erwin.Lugue | Exit door and staircase do not match.
50 | Call-out | 1 | RASHED SHOWAITER | Facts of T&Is from Bapco 6VDU: beds, distributors, beds structure support, beds hydrojetting, crane, et. Also, please find temp platform to take out beds from column, it is recommended to have big enough platform.
51 | Cloud+ | 1 | Ahmed Marhoon | For the analyzer house, contractor to ensure the following: 1. Size is adequate to accommodate the analyzers required per the unit design including all the utilities, SCSs ... etc taking into consideration the clearance spacings for maintenance activities. 2. Spare spaces are available for future use. Sparing requirement shall meet the same ratio specified in the typical analyzer house arrangement drawing BMPS-J-063862. 3. Location of the analyzer house is finalized taking into consideration the sample line length and conditions requirements according to BMPS-J23/ICM-DU-4363 in terms of ensuring a representative sample, minimizing lag time, process take-off and return, sample recovery system, accesses ...etc.
52 | Callout | 1 | Robert.Kawitzki | Full width access to transformers required
53 | Callout | 1 | Berik.Nurbolatov | GENERAL :Please ensure that 3 off decimals are used in elevation EL.
54 | Text Box | 1 | rob.urban | GENERAL COMMENT: OPTIMIZE PIPE RUNS AND OPTIMIZE EQUIPMENT LOCATION ACCORDING TO PROCESS FLOW, FOR EXAMPLE FROM P0001A/B CRUDE FEED GOES TO P010STR100 STRUCTURE AND THEN BACK AGAIN TO DESALTERS. VERY UNECONOMICAL AND CONSUMES UNNECESSARY RACK SPACE LINES RUNNING BACK AND FORTH
55 | Text Box | 1 | MAK | General Comment: The latest drawing borders have been submitted to JV Directorate on April 2018. Please use the latest drawing borders that are part of the Homogenisation Procedure.
56 | Call-out | 1 | MAK | General Comment: Use DD.MM.YYYY format for the date, e.g. 25.05.2018
57 | Text Box | 1 | Erwin.Lugue | General comments: Missing dimensions, & coordinates for locating equipments, roads, & structures
58 | Text Box | 1 | Mahdi Ali | General Comments: 1. All texts styles shall be consistent
59 | Text Box | 1 | alexis.martinez | General: All Equipment Numbers need to be updated as per the new numbering provided by owner. Review an d correct accordingly.
60 | Text Box | 1 | Ahmed Ali | General: TR to clarify the equipment numbers written between brackets and they requirement in the plot plan and wither they were written by mistake or not.
61 | Text Box | 1 | Berik.Nurbolatov | GENERAL;All distances b/n pumps, racks, units and roads should be shown on the plot plan.
62 | Text Box | 1 | Berik.Nurbolatov | GENERAL;Contractor to follow the requirements given on BMPS-A4,BMPS-A5 and BMPS-D5 on easy and safe maintenance and operation of the units by arranging free access to the personnel and cranes.
63 | Callout | 1 | Robert.Kawitzki | Has 20% piperack clearance on all levels been provided for future?
64 | Text Box | 1 | Robert.Kawitzki | Have all auto ignition pumps been placed on perimeter of the plot and are all high fire risk pieces of equipment covered by hydrants/monitors?
65 | Text Box | 1 | Robert.Kawitzki | Have all high pressure and high temperature equipment been placed close together to optimize pipe runs?
66 | Callout | 1 | Robert.Kawitzki | How will truck turn after accessing drop areas? This is way too far into the unit to reverse out. Safety issue
67 | Callout | 1 | Erwin.Lugue | HPP elevations missing
68 | Call-out | 1 | Mohamed Aldoseri | HVAC Room is missing in this drawing
69 | Callout | 1 | Erwin.Lugue | Identify hazardous areas with the necessity of spill control or containment- typ comment
70 | Callout | 1 | Erwin.Lugue | include all symbology and abbreviations
71 | Callout | 1 | Erwin.Lugue | Include in plan the doors access, platform for compressors, and removable panels, ramps (if reqd.) & access for maintenance
72 | Text Box | 1 | Robert.Kawitzki | Indicate where the main UG cable trench entry point is to SS
73 | Call-out | 1 | Ahmed Ali | is this for the valves battery limit as in the FEED? please include
74 | Call-out | 1 | RASHED SHOWAITER | Lay down area to be sufficient for unloading old structured packing, distributors, and grids. Also to be sufficient for new structured packing assembly.
75 | Callout | 1 | Erwin.Lugue | Locate expansion joints and ladders- typ comment
76 | Callout | 1 | Erwin.Lugue | Location?
77 | Callout | 1 | Erwin.Lugue | Location?
78 | Callout | 1 | Fernando.Perez | Lube Oil Console for compressors are required? If yes should be represented
79 | Call-out | 1 | Abdulaziz | Lube oil filling facility shall be considered with pneumatic drum pumps skid for crankcase and cylinder lubrication as per Bapco existing facility in H2 Make up compressors.
80 | Text Box | 1 | Abdulaziz | Lube oil station shall be of sufficient area to accommodate all types of lubricant and chemicals used where oil drums are placed on horizontal racks for easy handling.
81 | Callout | 1 | Erwin.Lugue | Missing coordinates & Elevations of roads
82 | Callout | 1 | Erwin.Lugue | Missing coordinates & Elevations of roads (typ. comment)
83 | Text Box | 1 | Erwin.Lugue | Missing covered shelter for lube oil & chemical storage as per vol 2 sec 6 sub 6.3.3- typ comment
84 | Callout | 1 | Erwin.Lugue | Missing drain slope & sump
85 | Callout | 1 | Erwin.Lugue | Missing drain slope & sump
86 | Callout | 1 | Erwin.Lugue | Missing guardposts, chain barricades, & crash barriers
87 | Callout | 1 | Erwin.Lugue | Missing location for emergency eyewash
88 | Callout | 1 | Erwin.Lugue | Missing location of fire protection facilities such as hydrants, sand bins, hose reel stations, & fire monitors
89 | Callout | 1 | Robert.Kawitzki | Move east away from SS to provide unencumbered access
90 | Callout | 1 | Robert.Kawitzki | Move staircase to north side of platform away from traffic turning circle
91 | Callout | 1 | Erwin.Lugue | No access?
92 | Callout | 1 | Erwin.Lugue | No section/elevation for this structure
93 | Callout | 1 | Robert.Kawitzki | Place drop area between compressors
94 | Callout | 1 | Berik.Nurbolatov | Please arrange SECTION VIEW
95 | Callout | 1 | Berik.Nurbolatov | Please arrange SECTION VIEW
96 | Callout | 1 | Berik.Nurbolatov | Please arrange SECTION VIEW
97 | Callout | 1 | Berik.Nurbolatov | Please mention HPP EL. relative to the site datum.
98 | Callout | 1 | Berik.Nurbolatov | Plot plans shall be dimensioned in metric units (mm) of linear measurement (refer BMPS A8 ‘General guidelines of Plot plan layout Part B Appendix B1 page 66)
99 | Callout | 1 | Erwin.Lugue | Provide area or space for erection of temporary lifts around atmospheric & vacuum columns, as per vol 5 WP2-Sec A 1.4
100 | Callout | 1 | Erwin.Lugue | Provide area or space for erection of temporary lifts around atmospheric & vacuum columns, as per vol 5 WP2-Sec A 1.4
101 | Callout | 1 | Robert.Kawitzki | Provide lift study for finfans - typ comment
102 | Callout | 1 | Robert.Kawitzki | Provide paved area infront of all transformers
103 | Callout | 1 | Robert.Kawitzki | Pump piping and pumps under structure. Confirm access
104 | Callout | 1 | Robert.Kawitzki | Pumps inaccessible
105 | Callout | 1 | Robert.Kawitzki | Pumps not to align or be close to rack columns if maintenance access is from under rack. Show that pump removal is possible over it's own motor
106 | Callout | 1 | Robert.Kawitzki | Pumps shall not align with rack columns if access is from under pipe rack - typ comment
107 | Callout | 1 | Erwin.Lugue | Refer to BMP-CON-LET-00047
108 | Callout | 1 | Erwin.Lugue | Reference coordinates of bundwall?
109 | Callout | 1 | Erwin.Lugue | Reference coordinates of bundwall?
110 | Callout | 1 | Erwin.Lugue | relative
111 | Callout | 1 | Erwin.Lugue | relative
112 | Callout | 1 | Erwin.Lugue | Roofing above transformers shall be removable, as per Vol 2, sec 6, sub sec. 6.3.3
113 | Callout | 1 | Robert.Kawitzki | Show bunding around pumps where required to ensure adequate clearance is provided - typ comment
114 | Callout | 1 | Robert.Kawitzki | Show clearance radius for all heaters
115 | Callout | 1 | Berik.Nurbolatov | Similar additional access is required for emergency case on the rack
116 | Callout | 1 | Erwin.Lugue | Specify location of expansion joints & ladders in piperacks
117 | Text Box | 1 | Erwin.Lugue | Street/plant lighting layout missing
118 |  | 1 | AutoCAD SHX Text | T
119 |  | 1 | AutoCAD SHX Text | T
120 |  | 1 | AutoCAD SHX Text | T
121 |  | 1 | AutoCAD SHX Text | T
122 |  | 1 | AutoCAD SHX Text | T
123 |  | 1 | AutoCAD SHX Text | The present document or drawing is property of TECHNIP ITALY S.p.A. and shall not, under any circumstances, be totally or partially, directly or indirectly, transferred, reproduced, copied, disclosed or used, without its prior written consent, for any purpose and in any way other than that for which it is specifically furnished or outside the extent of the agreed upon right of use.
124 | Call-out | 1 | Abdulaziz | To ensure that critical machine connected with vibration monitoring system are properly isolated from the surrounding structural vibration and mustn't affect any other machine during transient .
125 | Call-out | 1 | Abdulaziz | TR shall ensure that the bridge crane is of suitable capacity with sufficient safety factor to accommodate the compressors and its associated compartments. Please also demonstrate and proof that the crane can be operated safely to shift compressor heavy parts during major overhaul while the other compressor is in service. Dedicated lube oil station shall be considered for the reciprocating compressors due to the large oil quantity required for top up and PM lubrication.
126 | Text Box | 1 | RASHED SHOWAITER | TR to demonstrate the initial rigging study for maintenance and T&Is (post construction) and to consider the following: •Crane position and trailers for unloading and loading exchangers. •Crane position and trailers for exchangers using bundle-puller. •Crane position for vessels random packing. •Crane position for unloading and loading vacuum column structured packing. •Laydown assembly area for vacuum column structured packing. •Lifting of heavy control valves. •Lifting of RVs. •Lifting of pumps. •Crane position and trailers for fin fan bundles.
127 | Cloud+ | 1 | Mohamed Ayyash | Unable to read equipment number. Write it outside the sketch.
128 | Callout | 1 | Erwin.Lugue | Verify additional requirement for secondary egress, BMPS A5
129 | Callout | 1 | Erwin.Lugue | Verify additional requirement for secondary egress, BMPS A5
130 | Callout | 1 | Erwin.Lugue | Verify additional requirement for secondary egress, BMPS A5
131 | Callout | 1 | Erwin.Lugue | Verify additional requirement for secondary egress, BMPS A5
132 | Callout | 1 | Robert.Kawitzki | Verify clearance between pumps and buildings
133 | Callout | 1 | Erwin.Lugue | Verify grid numbering system
134 | Callout | 1 | Robert.Kawitzki | Verify how end of exchanger will be removed during shutdowns inside the structures - typ comment
135 | Callout | 1 | Erwin.Lugue | Verify if access platforms are required around the pumps
136 | Callout | 1 | Erwin.Lugue | Verify if access platforms are required around the pumps
137 | Text Box | 1 | Erwin.Lugue | Verify necessity in areas where overhead lifting, or cranes, platforms & shelters are typically required for frequent maintenance of reciprocating machines, recycle gas compressors, large size filters, & strainers as per vol 2 sec 6 sub 6.3.3- typ comment
138 | Callout | 1 | Erwin.Lugue | Verify necessity of monorails for maintenance of equipments or exchangers
139 | Callout | 1 | Erwin.Lugue | Verify necessity of monorails for maintenance of equipments or exchangers
140 | Callout | 1 | Erwin.Lugue | Verify necessity of monorails for maintenance of equipments or exchangers
141 | Callout | 1 | Erwin.Lugue | verify the adequacy of the spacing between the pumps and the structure so as not to have any vibration issues
142 | Callout | 1 | Erwin.Lugue | What are these?
143 | Callout | 1 | Robert.Kawitzki | What are these? PS?
144 | Callout | 1 | Robert.Kawitzki | What are these? T supports?
145 | Text Box | 1 | Robert.Kawitzki | Where is the HVAC? Rooftop? Confirm access
146 | Call-out | 1 | Ahmed Ali | with the relocation of these pumps, TR to ensure that there is crane access for the Atm. Column area