## 010-L-PPN-00001-003-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Erwin.Lugue | 011U0001- Is this necessary?
2 | Callout | 1 | Erwin.Lugue | 011U0001- Is this necessary?
3 | Callout | 1 | Erwin.Lugue | 011U0001- Is this necessary?
4 | Callout | 1 | Erwin.Lugue | Access ladders are missing
5 | Callout | 1 | Erwin.Lugue | Access?
6 | Text Box | 1 | Robert.Kawitzki | Are we allowing for a temporary lift for shutdowns on this unit? If yes, indicate location
7 | Callout | 1 | Erwin.Lugue | Clarify this symbol
8 | Callout | 1 | Erwin.Lugue | corresponds
9 | Callout | 1 | Berik.Nurbolatov | GENERAL :Please ensure that 3 off decimals are used in elevation EL.
10 | Text Box | 1 | alexis.martinez | General: All Equipment Numbers need to be updated as per the new numbering provided by owner. Review an d correct accordingly.
11 | Callout | 1 | Berik.Nurbolatov | GENERAL; Please arrange distance data b/ n grids , units. This will reload the overcrowded information given in main plot plan.
12 | Callout | 1 | Erwin.Lugue | Missing dimensions, & location of equipments- typ comment
13 | Callout | 1 | Erwin.Lugue | Missing dimensions, & location of equipments- typ comment
14 | Callout | 1 | Erwin.Lugue | Missing dimensions, & location of equipments- typ comment
15 | Callout | 1 | Erwin.Lugue | Missing handrails in plan
16 | Callout | 1 | Erwin.Lugue | Missing HPP elevation
17 | Callout | 1 | Erwin.Lugue | Missing levels of the platforms
18 | Callout | 1 | Erwin.Lugue | Move to center the title
19 | Callout | 1 | Berik.Nurbolatov | Please mention HPP EL. relative to the site datum.
20 | Callout | 1 | Berik.Nurbolatov | Please remove the plant orientation data as current plot plan is supplementary of the 010-L-PPN-00001-001. The reference can be made via grid data, elevation and rack name.
21 | Callout | 1 | Berik.Nurbolatov | Plot plans shall be dimensioned in metric units (mm) of linear measurement (refer BMPS A8 ‘General guidelines of Plot plan layout Part B Appendix B1 page 66)
22 | Callout | 1 | Erwin.Lugue | Provision for removal handrails for maintenance
23 | Callout | 1 | Erwin.Lugue | Refer to standard
24 | Callout | 1 | Erwin.Lugue | relative
25 | Callout | 1 | Erwin.Lugue | relative
26 | Callout | 1 | Erwin.Lugue | Reorganize grid numbering system
27 | Text Box | 1 | Robert.Kawitzki | Show ELs on side elevation - typ comment
28 | Text Box | 1 | 986131 | Side view/ elevation of the all the major columns and equipment in 7CDU and 7VDU are missing. Please add.
29 |  | 1 | AutoCAD SHX Text | The present document or drawing is property of TECHNIP ITALY S.p.A. and shall not, under any circumstances, be totally or partially, directly or indirectly, transferred, reproduced, copied, disclosed or used, without its prior written consent, for any purpose and in any way other than that for which it is specifically furnished or outside the extent of the agreed upon right of use.
30 | Callout | 1 | Erwin.Lugue | top of steel beam (T.O.S.)
31 | Text Box | 1 | RASHED SHOWAITER | TR to demonstrate the initial rigging study for maintenance and T&Is (post construction) and to consider the following: •Crane position and trailers for unloading and loading exchangers. •Crane position and trailers for exchangers using bundle-puller. •Crane position for vessels random packing. •Crane position for unloading and loading vacuum column structured packing. •Laydown assembly area for vacuum column structured packing. •Lifting of heavy control valves. •Lifting of RVs. •Lifting of pumps. •Crane position and trailers for fin fan bundles.
32 | Callout | 1 | Erwin.Lugue | Verify requirement for overhead lifting during maintenance
33 | Callout | 1 | Erwin.Lugue | Verify requirement for secondary egress as per BMPS A5
34 | Callout | 1 | Erwin.Lugue | Verify spacing for personnel access
35 | Callout | 1 | Erwin.Lugue | Verify sufficient spacing for access between equipments