## 010-P-STS-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | MAK | General Comment: Use the latest cover sheet which is part of the Homogenization Procedure. MOC shall coordinate with JV Directorate.
2 | Text Box | 1 | Mohamed Aldoseri | - Refer to comments in load balance no.2 HCU document (BMP-MOC-TRI-00076) and incorporate in this document. - Ensure all details are read in conjuction with relevant SLD.
3 | Call-out | 2 | Mohamed Aldoseri | 7 CDU Substation
4 | Text Box | 2 | Mahdi Ali | 7CDU
5 | Text Box | 2 | CK Samy | Please include following in the load balance 1. Type of service (Normal feeding / Emergency) 2. Load status (preliminary 'P' and Final 'F' 3. brake kW at pump shaft shall be multiplied by following service factor as per API 610 to select standard motor rating. a. MF 1.25 is applied up to 22kW b. MF1.15 is applied between 22kW and 55kW c. MF 1.1 is applied beyond 55kW 5. Equipment type a. Motor b. panel (UPS,PDB,Heater,Welding socket) 6. IEC typical efficiency and power factor values shall be used during preliminary load phase.
6 | Text Box | 3 | Ahmed Marhoon | Instrumentation and Control Comments. The following comments are applicable to all load balance lists: 1. Contractor to ensure that all power supply consumers for the instrumentation and control are detailed/included in compliance with the applicable BMPS specifications such as J1, J14, P1 ...etc. All redundant power supplies (including UPS & non-UPS) for safety and non-safety related to be considered/added (DCS, ESD, GAS, FAS, MCM, PLC ...etc) in the list. 2. All power supply consumers for field standalone control systems, if any, to be considered/added. 3. Satellite Rack Rooms details (including building numbers) to be updated based on the latest SRR building design/numbers. 4. List to be updated based on the detail engineering development to include any new requirements based on selected instrument models/vendors such field instruments requiring external 110 VAC power supply (e.g. some Ultrasonic flow meters). 5. Ensure to include the Analyzers/Analyzer Houses. 6. The development in the new refinery centralized control building shall be considered in this list.
7 | Call-out | 3 | CK Samy | ** refer to what?
8 | Text Box | 3 | Mohamed Aldoseri | - Refer to comments in load balance no.2 HCU document (BMP-MOC-TRI-00076). - Ensure all details are read in conjuction with relevant SLD.
9 | Text Box | 3 | CK Samy | Minimum 25% spare during DE and 20% at the time of completion
10 | Ellipse | 3 | CK Samy
11 | Call-out | 3 | CK Samy | Bapco Equipment numbers to be used for switchgear buses and Transformers.
12 | Ellipse | 3 | CK Samy
13 | Call-out | 4 | CK Samy | Not required- repeated info in Bus section
14 | Call-out | 4 | CK Samy | All load factor shall be checked and corrected (typical and applies to all SWBD)
15 | Call-out | 4 | CK Samy | SWBD Voltage rating explanation to be included in page 2. * 2 - 11 Kv * 3 - 6.6 kv * 4 - 400v
16 | Cloud+ | 18 | Mohamed Ayyash | Replace "ATM" with ATMOS
17 | Cloud+ | 18 | Mohamed Ayyash | Replace "ATM" with ATMOS
18 | Call-out | 19 | CK Samy | Use correct switchboard & MOV tag numbering.(typical)