## 010-S-DAT-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Fernando.Perez | Chemical Injection Package to follow BMPS-S10 spec.
| Text Box | 1 | Ahmed Marhoon | The following are comments related to instrumentation and control. Contractor is requested to update the other documents that will be issued part of the RFI based on the comments stated herein and ensure consistency prior to release of MR to suppliers. 1. All applicable BMPS from J class to be added for the supplier to comply with (e.g. J6, J2, J31 ... etc). Suppliers to be instructed to design all instruments and control systems according to BMPS specifications. This document does not contain the required reference to BMPS-J specs. 2. Supplier to be instructed to generate all instrument data sheets, hook ups ...etc. in project specs (according to Client standard formats) and to be developed in SPI format. Typical formats can be provided to the supplier at a later stage for compliance. In addition to BMPS J Specifications, all relevant BMPS J Standard/Typical Drawings to be included. 3. Supplier to be instructed to source all instrumentation from the approved AVL for BMP. 4. Narrative/flow charts/cause and effect shall be provided, in Client standard formats, for any control or sequence logic. 5. Add a note to the supplier to design, fabricate and supply the instruments in accordance with the BMPS J specifications. Items such as Junction boxes, cables, wiring, ferruling, earthing, terminal strips, fitting …etc shall be installed by the vendor/contractor meeting the requirements specified on the applicable BMPS J specifications like BMPS-J31. 6. Add a note to the supplier with reference to the applicable BMPS to design and supply the system according to the final PID. Functional design specifications covered in this document shall be firmed based on the approved PID. Vendors to be clearly notified on the necessity to include all the Hazop3/SIL recommendations and changes made Post-EPC-Development. 7. With reference to Note 16 on sheet 3, the preference in BMP is to have all control being performed in the plant DCS and safety function in plant ESD. In occasions where this is technically not feasible, local control panels are to be installed in Satellite Rack Rooms as specified in BMPS-J6 with the necessary interface with DCS. Technical requirements such as segregation between high voltage electrical components and low voltage instrument components, signal/connections types/protocols ...etc shall comply with BMPS-J6/J2/J31 and suppliers to be instructed to do so. Contractor to clarify the intent of the note. 8. Vendor/TTSJV shall provide a list of deviation from BMPS specifications, in addition to the requisition specifications, for owner's review and approval.
2 | Text Box | 1 | 986131 | The package definition does not provide the process details for the vendor to select the chemical and decide on the injection rate required. What is the performance that we want the vendor to meet? And Guarantees expected from the injection, if any? Please discuss with the vendor and add the required process details to technically specify the package requirements. Please attached the relevant P&ID's to definer the battery limit.
3 | Call-out | 2 | Abdulaziz | Missing information to be added and apply for all pages
4 | Call-out | 3 | Abdulaziz | Maximum and rated capacity to be shown as per BMPS S10
5 | Call-out | 3 | Abdulaziz | Not recommended as failure of any component/head means losing the whole 5 heads as its driven by one motor.
6 | Cloud+ | 3 | 986131 | Note 33: This note is not clear. Please explain what it means by 5-heads pumps.
7 | Call-out | 3 | Abdulaziz | Pump supplier shall provide assurance of pumps reliability in similar service and duty point as we have encountered a lot of issues related to performance after short life span in Bapco.
8 | Call-out | 3 | Ahmed Marhoon | Verify and confirm the number of pumps (installed and spare) with respect to P&ID.