## 010-S-DAT-00003-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Fernando.Perez | Chemical Injection Package to follow BMPS-S10 spec.
2 | Text Box | 1 | 986131 | The package definition does not provide the process details for the vendor to select the chemical and decide on the injection rate required. What is the performance that we want the vendor to meet? And Guarantees expected from the injection, if any? Please discuss with the vendor and add the required process details to technically specify the package requirements. Please attached the relevant P&ID's to definer the battery limit.
3 | Call-out | 2 | Ahmed Ali | injection
4 | Call-out | 2 | Abdulaziz | Missing information to be added and apply for all pages
5 | Call-out | 3 | Abdulaziz | Maximum and rated capacity to be shown as per BMPS S10
6 | Call-out | 3 | Abdulaziz | Pump supplier shall provide assurance of pumps reliability in similar service and duty point as we have encountered a lot of issues related to performance after short life span in Bapco.
7 | Call-out | 3 | Sameer Foujdar | Typo error should read as Absorber