## 019-E-DAT-00039-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Typewritten Text | 1 | Mohamed Ayyash | General comment: Many text fonts are small and unreadable. Need to enlarge.
2 | Text Box | 1 | Mahdi Ali | Remove letter 'c'
3 | Text Box | 1 | MAK | Use the latest document cover page template which is part of the Homogenization Procedure. MOC Contractor shall coordinate with JV Directorate.
4 | Callout | 2 | Yousif Ahmadi | Minimum
5 | Call-out | 2 | Abdulaziz | Missing information to be provided
6 | Callout | 2 | Yousif Ahmadi | Per FEED it is plug type. TR to clarify tthe double plug type selection
7 | Cloud+ | 2 | A.Jabbar Mahmood | TR to add a note reporting the air conditions (temp, density and barometric pressure) on which this value based on (Typical comment for aircooler d/s).
8 | Call-out | 2 | Abdulaziz | TR to clarify no. of vibration switch on the finfans bundle/bank
9 | Text Box | 4 | Ahmed Marhoon | 1. Reference to note 14: The scope for instrumentation and control is not limited to the alarms in DCS only. All the control functions will be done in the DCS with the necessary interconnections with the electrical MCC. A clear note to be added to emphasize on having the temperature control by the outlet temperature measurement. The final design of the system shall be based on the BMPS specifications (including relevant J class) and the final PID post detail design and Hazop3/SIL analysis. Suppliers to be instructed accordingly. This is a typical comment for all fin fan air coolers. 2. Contractor to add reference to the applicable BMPS specifications such as BMPS-P20/P21 and relevant BMPS-J specifications. Typical for all air coolers with Variable Speed Drives.
10 | Callout | 4 | Yousif Ahmadi | Add note 10 of FEED data sheet: "Two fans per bay shall be provided as minimum."
11 | Text Box | 4 | Omran A | As per BMPS-J36, BMPS-J37 & BMPS-J38
12 | Call-out | 4 | A.Jabbar Mahmood | correct font size of note 8
13 | Text Box | 4 | Abdulaziz | Fin fan shaft bearings shall be furnished with vibration sensors that are connected to a junction box e.g. Switch Box SB 202 with 48 channels provided at platform. This will provide convenient provision to collect the vibration data using 2140 portable vibration analyzer.
14 | Cloud+ | 4 | A.Jabbar Mahmood | Owner (MOC) has not seen this TQ.
15 | Cloud+ | 4 | A.Jabbar Mahmood | Owner team in MOC has not seen this document. TR to provide for reference
16 | Callout | 4 | Yousif Ahmadi | This should be strength welded as per FEED data sheet
17 | Call-out | 4 | A.Jabbar Mahmood | TR to ensure that the design temperature is adequate for the starting up conditions when the pump-arounds are not yet in operation, as explained in the ITB (SOW) and discussed during the P&IDs review.
18 | Text Box | 4 | Mahdi Ali | Use Bapco number