## 019-E-DAT-00040-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Typewritten Text | 1 | Mohamed Ayyash | General comment: Many text fonts are small and unreadable. Need to enlarge.
2 | Text Box | 1 | Mahdi Ali | Remove letter 'c'
3 | Text Box | 1 | MAK | Use the latest document cover page template which is part of the Homogenization Procedure. MOC Contractor shall coordinate with JV Directorate.
4 | Callout | 2 | Yousif Ahmadi | Change the Blade material in the MSD
5 | Callout | 2 | Yousif Ahmadi | Minimum
6 | Call-out | 2 | Abdulaziz | Missing information to be provided
7 | Call-out | 2 | Abdulaziz | TR to clarify no. of vibration switch on the finfans bundle/bank
8 | Text Box | 3 | Mahdi Ali | 9 or 19?
9 | Text Box | 3 | Omran A | As per BMPS-J36, BMPS-J37 & BMPS-J38
10 | Cloud+ | 3 | A.Jabbar Mahmood | correct the pump no. to 019P0009A/B
11 | Text Box | 3 | Abdulaziz | Fin fan shaft bearings shall be furnished with vibration sensors that are connected to a junction box e.g. Switch Box SB 202 with 48 channels provided at platform. This will provide convenient provision to collect the vibration data using 2140 portable vibration analyzer.
12 | Callout | 3 | Yousif Ahmadi | This is not per MSD and note 8 of FEED data sheet
13 | Text Box | 3 | Mahdi Ali | Use Bapco number
14 | Text Box | 3 | Ahmed Marhoon | With reference to note 14, the scope for instrumentation and control is not limited to the alarms in DCS. All the control functions will be done in the DCS with the necessary interconnections with the electrical MCC. The final design of the system shall be based on the BMPS specifications (including relevant J class) and the final PID post detail design and Hazop3/SIL analysis. Suppliers to be instructed accordingly.