## 019-E-DAT-00042-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Typewritten Text | 1 | Mohamed Ayyash | General comment: Many text fonts are small and unreadable. Need to enlarge.
2 | Text Box | 1 | Mahdi Ali | Remove letter 'c'
3 | Text Box | 1 | MAK | Use the latest document cover page template which is part of the Homogenization Procedure. MOC Contractor shall coordinate with JV Directorate.
4 | Callout | 2 | Yousif Ahmadi | Change the Blade material in the MSD
5 | Callout | 2 | Yousif Ahmadi | Minimum
6 | Call-out | 2 | Abdulaziz | Missing information to be provided
7 | Call-out | 2 | Abdulaziz | TR to clarify no. of vibration switch on the finfans bundle/bank
8 | Call-out | 3 | Abdulaziz | Missing information to be provided
9 | Call-out | 3 | A.Jabbar Mahmood | Review the requirement of louvers for temp control due to climate change to avoid congealing.
10 | Call-out | 3 | Abdulaziz | TR to clarify no. of vibration switch on the finfans bundle/bank
11 | Text Box | 4 | Ahmed Marhoon | 1. Reference to notes 14: The scope for instrumentation and control is not limited to the alarms in DCS only. All the control functions will be done in the DCS with the necessary interconnections with the electrical MCC. The final design of the system shall be based on the BMPS specifications (including relevant J class) and the final PID post detail design and Hazop3/SIL analysis. Suppliers to be instructed accordingly. This is a typical comment for all fin fan air coolers. 2. Contractor to add reference to the applicable BMPS specifications such as BMPS-P20/P21 and relevant BMPS-J specifications. Typical for all air coolers with Variable Speed Drives.
12 | Text Box | 4 | Omran A | As per BMPS-J36, BMPS-J37 & BMPS-J38
13 | Cloud+ | 4 | A.Jabbar Mahmood | As per the P&IDs, 60# steam is used for the winterizing coil. Anyway, as discussed TR is supposed to evaluate using 60# versus 110# steam and confirm which one provides better performance considering the steam conditions. Accordingly, this datasheet and P&IDs shall be updated.
14 | Cloud+ | 4 | A.Jabbar Mahmood | correct pump no. to 019P0017A/B
15 | Text Box | 4 | Mahdi Ali | Equipment no. to be as per BMPS-A8
16 | Text Box | 4 | Abdulaziz | Fin fan shaft bearings shall be furnished with vibration sensors that are connected to a junction box e.g. Switch Box SB 202 with 48 channels provided at platform. This will provide convenient provision to collect the vibration data using 2140 portable vibration analyzer.
17 | Call-out | 4 | Sameer Foujdar | Rephrase the statement 2nd stage feed from E0032 to slops via E0034.
18 | Text Box | 4 | A.Jabbar Mahmood | Review and consider the requirement of skin temperature measurement for monitoring and control to avoid congealing