## 019-L-PPN-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 |  | 1 | AutoCAD SHX Text | - C/Arapiles 14, Madrid, Spain
2 | Call-out | 1 | Sameer Foujdar | No details of this strucutre provided.
3 | Call-out | 1 | MAK | 019 - NO. 2 HYDROCRACKING UNIT
4 | Text Box | 1 | Ahmed Marhoon | 1. Contractor to ensure that underground cable trench size and design is adequate to accommodate all the underground multipair cables with the necessary segregation from high voltage electrical trenches and 30% spare space for future use as per the BMPS-J series. Any deviation from this requirement shall be brought to owner's attention for review/evaluation. 2. Analyzers if not installed in ventilated analyzer house, shall be installed in field shelters. Contractor to consider space for these analyzers with the necessary access in the plot plan. In addition to the analyzers designed to be in analyzer house, there are other analyzers in the plant that need to be installed under shades.
5 | Text Box | 1 | rob.urban | 19V0005 TO BE IN SAME STRUCTURE AS 019C0003 (MINIMUM DISTANCE)
6 | Text Box | 1 | RASHED SHOWAITER | 1ST AND 2ND STAGE REACTOR TOP ELBOWS [CAT CHANGE]
7 | Text Box | 1 | RASHED SHOWAITER | AC [CAT CHANGE]
8 | Callout | 1 | Robert.Kawitzki | All common centerlines to be located
9 | Text Box | 1 | RASHED SHOWAITER | BA BUS [CAT CHANGE]
10 | Text Box | 1 | RASHED SHOWAITER | BA CONTAINER [CAT CHANGE]
11 | Call-out | 1 | Hasan Al Noaimi | catalyst area has to be paved and should not be cravels.
12 | Callout | 1 | Robert.Kawitzki | Catalyst area to be paved - typical comment
13 | Call-out | 1 | Hasan Al Noaimi | catalyst area to be paved. NO cravels.
14 | Call-out | 1 | MAK | Change L to A which is the correct Material Class for Plot Plan.
15 | Call-out | 1 | Sameer Foujdar | Chemical and oil storage area should have oil spill containment area and concrete surface to avoid oil slippage to ground.
16 | Cloud+ | 1 | Mohamed Ayyash | Clarify this curved line ?
17 | Callout | 1 | Robert.Kawitzki | Confirm that 20% future room has been provided on all levels of all pipe racks
18 | Cloud+ | 1 | Ahmed Marhoon | Contractor to confirm the location of the analyzer house with reference to proximity to the sample point. It is noticed that the current location is far away from the battery limit arrangement which is normally closer to the analyzer house. Check and confirm.
19 | Text Box | 1 | Erwin.Lugue | corresponds
20 | Call-out | 1 | Sameer Foujdar | Crane access to HP Exchangers, 0190003, and preheat exchangers will be blocked during catalyst loading and unloading activities.
21 | Call-out | 1 | Sameer Foujdar | Crane access to Make-up Hydrogen compressors interstage exchangers will be blocked during catalyst loading and unloading activities.
22 | Text Box | 1 | RASHED SHOWAITER | CRANE POSITION FOR 1ST STAGE REACTOR [CAT CHANGE]
23 | Text Box | 1 | RASHED SHOWAITER | CRANE POSITION FOR 2ND STAGE REACTOR [CAT CHANGE]
24 | Call-out | 1 | Abdulaziz | Crank case and cylinder lubricators lube oil filing facility with pneumatic drum pump connected to oil dispensers located near by each compressor.
25 | Callout | 1 | Erwin.Lugue | Curb?
26 | Call-out | 1 | MAK | Delete C and never use prefixes for Unit Nos.
27 | Call-out | 1 | MAK | Delete. This is for Bapco use.
28 | Call-out | 1 | Sameer Foujdar | Details of all the platforms in this Plot plan to be provided in 019-L-PPN-00001-002-RA
29 | Text Box | 1 | RASHED SHOWAITER | DUST FILTER [CAT CHANGE]
30 | Text Box | 1 | RASHED SHOWAITER | DUST FILTER [CAT CHANGE]
31 | Text Box | 1 | RASHED SHOWAITER | DUST FILTER [CAT CHANGE]
32 | Call-out | 1 | Sameer Foujdar | Elevation details to be provided for 019STR500
33 | Call-out | 1 | Sameer Foujdar | Elevation details to be provided for C019PR600
34 | Cloud+ | 1 | Mohamed Ayyash | Enlarge font
35 | Cloud+ | 1 | Mohamed Ayyash | Enlarge font
36 | Cloud+ | 1 | Mohamed Ayyash | Enlarge font
37 | Cloud+ | 1 | Mohamed Ayyash | Enlarge font
38 | Cloud+ | 1 | Mohamed Ayyash | Enlarge font
39 | Cloud+ | 1 | Mohamed Ayyash | Enlarge font
40 | Cloud+ | 1 | Mohamed Ayyash | Enlarge font
41 | Callout | 1 | Robert.Kawitzki | Ensure adequate room is provided between exchangers including piping and valves - typical comment
42 | Callout | 1 | Robert.Kawitzki | Ensure that when equipment is located inside a structure, that adequate room is provided including piping, valve actuators, instruments etc
43 | Call-out | 1 | Sameer Foujdar | Equipment layout is not shown hence maintenance access is a concern.
44 | Callout | 1 | Robert.Kawitzki | Extend building and add drop area for 019K0004. No lift over working compressor
45 | Text Box | 1 | RASHED SHOWAITER | FORKLIFT MOVEMENT [CAT CHANGE]
46 | Text Box | 1 | RASHED SHOWAITER | FORKLIFT MOVEMENT [CAT CHANGE]
47 | Text Box | 1 | RASHED SHOWAITER | FRESH CATALYST LOADING [CAT CHANGE]
48 | Text Box | 1 | RASHED SHOWAITER | FRESH CATALYST LOADING [CAT CHANGE]
49 | Callout | 1 | Berik.Nurbolatov | GENERAL :Please ensure that 3 off decimals are used in elevation EL.
50 | Text Box | 1 | rob.urban | GENERAL COMMENT: RE-ARRANGE EQUIPMENT LAY-OUT SUCH THAT PIPING LENGTH IN HP LOOP IS MINIMIZED. NOW HP EQUIPMENT IS SPREAD ALL OVER THE UNIT AND HP PIPING IS NOT OPTIMIZED. FOLLOW THE PROCESS FLOW. STACK MORE EQUIPMENT TO MAKE SPACE ON THE PLOT. FRACTIONATION SECTION EQUIPMENT SHOULD NOT BE IN REACTOR SECTION
51 | Text Box | 1 | MAK | General Comment: The latest drawing borders have been submitted to JV Directorate on April 2018. Please use the latest drawing borders that are part of the Homogenisation Procedure.
52 | Call-out | 1 | MAK | General Comment: Use DD.MM.YYYY format for the date, e.g. 25.05.2018
53 | Text Box | 1 | Berik.Nurbolatov | GENERAL:Please consider crane access to process rack and pumps .
54 | Text Box | 1 | Berik.Nurbolatov | GENERAL; Contractor to follow the requirements given on BMPS-A4,BMPS-A5 and BMPS-D5 on easy and safe maintenance and operation of the units by arranging free access to the personnel and cranes.
55 | Text Box | 1 | Berik.Nurbolatov | GENERAL;All distances b/n pumps, racks, units and roads should be shown on the plot plan.
56 | Text Box | 1 | RASHED SHOWAITER | GENERATOR [CAT CHANGE]
57 | Callout | 1 | Erwin.Lugue | Grid numbering has to be reorganized
58 | Text Box | 1 | RASHED SHOWAITER | HOPPER CYCLONE[CAT CHANGE]
59 | Call-out | 1 | RASHED SHOWAITER | HOW THE CRANE WILL REACH FORT&IS
60 | Call-out | 1 | Hasan Al Noaimi | how the motors of the fans are removed
61 | Callout | 1 | Robert.Kawitzki | I assume that pipes will run from PLF100 to PR100? If yes then align columns for pipe clearance and relocate staircase. If pipes will run to the main rack a battery limit needs to be indicated
62 | Text Box | 1 | Erwin.Lugue | Identify hazardous areas that may require spill control or containment
63 | Text Box | 1 | Ahmed Marhoon | In general, contractor to ensure the following: 1. Size is adequate to accommodate the analyzers required per the unit design including all the utilities, SCSs ... etc taking into consideration the clearance spac-ings for maintenance activities. 2. Spare spaces are available for future use. Sparing requirement shall meet the same ratio specified in the typical analyzer house arrangement drawing BMPS-J-063862. 3. Location of the analyzer house is finalized taking into consideration the sample line length and conditions requirements according to BMPS-J23/ICM-DU-4363 in terms of ensuring a representative sample, minimizing lag time, process take-off and return, sample recovery system, accesses ...etc.
64 | Callout | 1 | Erwin.Lugue | Include all symbology and abbreviations
65 | Callout | 1 | Erwin.Lugue | Indicate location of crane platform, requirement for overhead lifting
66 | Callout | 1 | Robert.Kawitzki | Is it possible to stack some exchangers to give a bit more room on the plot? Couple of places where this is possibleVery congested plot plan
67 | Callout | 1 | Robert.Kawitzki | Is there enough access room around the pumps. Consider piping, valves, instruments etc - typical comment
68 | Callout | 1 | Robert.Kawitzki | Is this a pit? If so, add EL TOC and show access ladders. Truck access should be done without reversing (flagman required if this is not the case)
69 | Callout | 1 | Robert.Kawitzki | Keep access clear for drop zone when considering placement of analyzer house
70 | Callout | 1 | Erwin.Lugue | Ladder or stairs not shown to access the platform
71 | Call-out | 1 | Abdulaziz | Lifting rails to be provided for fin fans to facilitate the removal of motor for repair. Typical for all air coolers
72 | Callout | 1 | Erwin.Lugue | Location?
73 | Callout | 1 | Erwin.Lugue | Location?
74 | Call-out | 1 | Abdulaziz | Lube oil purifier shall be considered with the lube oil package.
75 | Call-out | 1 | Abdulaziz | Lube oil shelter shall provided for the reciprocating compressor lubricants
76 | Callout | 1 | Robert.Kawitzki | Maintenance
77 | Callout | 1 | Robert.Kawitzki | Minimum width for access roads to be 4000mm - typical comment
78 | Callout | 1 | Erwin.Lugue | Missing access stair or ladder to this platform
79 | Callout | 1 | Erwin.Lugue | Missing access stair or ladder to this platform
80 | Callout | 1 | Erwin.Lugue | Missing access stair or ladder to this platform
81 | Callout | 1 | Erwin.Lugue | Missing coordinates & elevations in road intersections- typ. comment
82 | Callout | 1 | Erwin.Lugue | Missing details of platform. Provide section
83 | Callout | 1 | Erwin.Lugue | Missing details of platform. Provide section
84 | Text Box | 1 | Erwin.Lugue | Missing dimensions and coordinates for locating equipments and structures
85 | Text Box | 1 | Erwin.Lugue | Missing HPP elevation
86 | Callout | 1 | Erwin.Lugue | Missing location of chain barriers, guardposts, crash barriers
87 | Callout | 1 | Erwin.Lugue | Missing location of firefighting facilities, such as sand bins, hydrants, hose reels, & fire monitors
88 | Callout | 1 | Robert.Kawitzki | Move stairs away from access way. Safety issue and trucks will wipe this out
89 | Text Box | 1 | RASHED SHOWAITER | NITROGEN CIRCULATION UNIT LONE[CAT CHANGE]
90 | Callout | 1 | Erwin.Lugue | No section & details of this platform
91 | Callout | 1 | Erwin.Lugue | No section & details of this platform
92 | Call-out | 1 | Hasan Al Noaimi | No2
93 | Text Box | 1 | Antony.Bentley | NOTE: PLOT PLAN MODIFICATION WRT S/STN RR CANNOT BE ACCEPTED WITHOUT FULL PLOT PLAN EVALUATION EXERCISE - SEE RESPONSE TO R-TCQ-0002
94 | Call-out | 1 | Abdulaziz | OMG location to be revised
95 | Callout | 1 | Robert.Kawitzki | Paved access to main load platform required
96 | Callout | 1 | Robert.Kawitzki | Place all columns on the same centerline
97 | Callout | 1 | Erwin.Lugue | Platform?
98 | Callout | 1 | Berik.Nurbolatov | Please mention HPP Grade El.relative to site datum.
99 | Callout | 1 | Berik.Nurbolatov | Plot plans shall be dimensioned in metric units (mm) of linear measurement (refer BMPS A8 ‘General guidelines of Plot plan layout Part B Appendix B1
100 | Callout | 1 | Robert.Kawitzki | Provide access road for under rack access
101 | Callout | 1 | Erwin.Lugue | Provide minimum area for lube oil & chemical storage as per BMPS vol 2 sub 6. sub. sec 6.3.3
102 | Callout | 1 | Robert.Kawitzki | Provide removal and lift study for pumps and motors
103 | Callout | 1 | Robert.Kawitzki | Provide turn in radius for access roads - typical comment
104 | Text Box | 1 | Abdulaziz | Pumps area is congested and shall be reviewed for proper maintenance access considering all auxiliaries and seal support that extend beyond the baseplate.
105 | Cloud+ | 1 | Sameer Foujdar | Pumps on auto ignition temperature to be considered to locate at road side for safety concerns.
106 | Call-out | 1 | Mahdi Ali | Quote the EPC phase drawing number. 000-A-PPN-60001-001
107 | Callout | 1 | Robert.Kawitzki | Really? Bapco does not prepare, nor check drawings
108 | Callout | 1 | Erwin.Lugue | Refer to BMP-CON-LET-00047
109 | Text Box | 1 | Robert.Kawitzki | Reference plant datum drawing
110 | Text Box | 1 | Erwin.Lugue | relative
111 | Text Box | 1 | Erwin.Lugue | relative
112 | Text Box | 1 | Robert.Kawitzki | REVIEW
113 | Callout | 1 | Erwin.Lugue | Road? Clarify this curved line
114 | Callout | 1 | Erwin.Lugue | Road? Clarify this curved line
115 | Callout | 1 | Robert.Kawitzki | Sections and elevations to be shown for all structures
116 | Callout | 1 | Erwin.Lugue | Show access, stairs or ladders to air coolers
117 | Callout | 1 | Erwin.Lugue | Show access, stairs or ladders to air coolers
118 | Callout | 1 | Robert.Kawitzki | Show common discharge centerline for pumps
119 | Callout | 1 | Erwin.Lugue | Show location of expansion joints and dimensions on piperacks- typ comments
120 | Callout | 1 | Erwin.Lugue | Show location of expansion joints and dimensions on piperacks- typ comments
121 | Callout | 1 | Erwin.Lugue | Show location of expansion joints and dimensions on piperacks- typ comments
122 | Callout | 1 | Erwin.Lugue | Show locations of emergency eyewash
123 | Callout | 1 | Robert.Kawitzki | Show overhead crane
124 | Callout | 1 | Robert.Kawitzki | Show radius full width maintenance access to ensure trucks can turn safely
125 | Callout | 1 | Robert.Kawitzki | Show staircase and/or vertical ladders - typical comment
126 | Callout | 1 | Robert.Kawitzki | Show study that all finfans are accessible with a crane
127 | Callout | 1 | Erwin.Lugue | Show the doors, & access ramps
128 | Text Box | 1 | Erwin.Lugue | Street /plant lighting location missing
129 | Callout | 1 | Erwin.Lugue | Structural platform not defined? Provide section
130 | Callout | 1 | Robert.Kawitzki | Sufficient room for bundle pulling equipment?
131 | Callout | 1 | Robert.Kawitzki | Text height as per BMPS A8 - typ comment
132 |  | 1 | AutoCAD SHX Text | The present document or drawing is property of TECHNIP ITALY S.p.A. and shall not, under any circumstances, be totally or partially, directly or indirectly, transferred, reproduced, copied, disclosed or used, without its prior written consent, for any purpose and in any way other than that for which it is specifically furnished or outside the extent of the agreed upon right of use.
133 | Callout | 1 | Robert.Kawitzki | This is truck access. Trucks do not turn around 90 degree corners
134 | Call-out | 1 | Hasan Al Noaimi | This maintenance area for K2 and K 3 what about K4. Loaded overhead crane should not pass over LIVE machines
135 | Call-out | 1 | Abdulaziz | To provide enough space B/W pump and oil console for easy access and maintenance.
136 | Callout | 1 | Robert.Kawitzki | Too narrow for truck access to drop area. Align access way to road that truck has straight access route. How is truck going to be loaded?
137 | Text Box | 1 | A.Jabbar Mahmood | TR to also consider making these areas available for catalyst laydown as the allocated catalyst laydown area seems to be tight.
138 | Text Box | 1 | RASHED SHOWAITER | TR to demonstrate the initial rigging study for maintenance and T&Is (post construction) and to consider the following: •Catalyst Change Crane Parking. •Catalyst Change equipment and activities, such as, catalyst bags, hoppers, loading area, forklift movement, etc. •Crane position and trailers for unloading and loading exchangers. •Crane position and trailers for exchangers using bundle-puller. •Crane position for vessels random packing. •Lifting of heavy control valves. •Lifting of RVs. •Lifting of pumps. •Crane position and trailers for fin fan bundles.
139 | Text Box | 1 | A.Jabbar Mahmood | TR to refer to the attached word file which explains the catalyst unloading and loading activity based on Owner's extensive experience and ensure that sufficient plot space is available for performing the catalyst changeout activity safely and efficiently, without delays. Delays in catalyst changeout can be very costly (more than 1 US$ million for each day).
140 | Call-out | 1 | Abdulaziz | Typo; Shall be corrected.
141 | Callout | 1 | Robert.Kawitzki | Use different font than centerline
142 | Text Box | 1 | RASHED SHOWAITER | VACUUM TRUCK [CAT CHANGE]
143 | Text Box | 1 | RASHED SHOWAITER | VACUUM TRUCK [CAT CHANGE]
144 | Callout | 1 | Erwin.Lugue | verify column orientation
145 | Callout | 1 | Erwin.Lugue | Verify extent of platform requirement
146 | Callout | 1 | Erwin.Lugue | verify extent of platform to service the pumps
147 | Callout | 1 | Erwin.Lugue | Verify if no siding, partially, and or fully enclosed shelter
148 | Callout | 1 | Erwin.Lugue | verify maximum direct distance requirements from the door to the stairs
149 | Callout | 1 | Erwin.Lugue | Verify platform requirement for this vessel
150 | Callout | 1 | Erwin.Lugue | Verify requirement for removable roof panel in the drop area
151 | Callout | 1 | Erwin.Lugue | Verify requirement for secondary egress as per BMP A5
152 | Callout | 1 | Erwin.Lugue | Verify requirement of removable panels for maintenance
153 | Text Box | 1 | Robert.Kawitzki | Verify that all high temperature and all high pressure equipment has been logically placed close together to minimize pipe run lengths and optimize available room in the pipe racks
154 | Callout | 1 | Robert.Kawitzki | Verify that bundle pulling equipment has enough room to operate
155 | Call-out | 1 | Hasan Al Noaimi | what about Lube oil area
156 | Callout | 1 | Robert.Kawitzki | What do these pumps service? How is the pipe going to be routed?
157 | Callout | 1 | Robert.Kawitzki | What is the distance between main and spur rack. Keep max pipe span distances in mind - typical comment
158 | Callout | 1 | Robert.Kawitzki | Where is a proposed vehicle parking area for this unit?
159 | Callout | 1 | Robert.Kawitzki | Where is the access to the drop area?
160 | Callout | 1 | Robert.Kawitzki | Where is the main double door and loading platform for this SS?
161 | Callout | 1 | Robert.Kawitzki | Why are the pumps so far west of structure? Move east
162 | Callout | 1 | Robert.Kawitzki | Why are these pumps so far away from the rack?
163 | Callout | 1 | Robert.Kawitzki | Why are these pumps so far away from the rack? How are the pipes going to run? Align discharge lines
164 | Callout | 1 | Robert.Kawitzki | Why aren't the discharge centerlines aligned?
165 | Callout | 1 | Robert.Kawitzki | Widen maintenance access and access road to give full front access for pump maintenance