## 041-G-DAT-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Nalini Mohan | All fields in the datasheet shall be filled. If the field is not applicable include as N/A
2 | Text Box | 1 | BD Mori | Comments on this data sheet are also applicable to 042P0001A/B and 043P0001A/B
3 | Text Box | 1 | Nalini Mohan | The document is approved as Code 2 subject to incorporation of information obtained during subsequent detailed engineering development. Prior to issue of the PO the datasheet shall include all the updated details and be in code 2 approval status.
4 | Text Box | 1 | MAK | This datasheet template was revised and will be issued with the Homogenization Procedure. In the next revision, the revised template shall be used.
5 | Callout | 2 | Dowon Pyun | Contractor to confirm the min. 110% of design flowrate as per specification requirement
6 | Callout | 2 | BD Mori | General comment for all the data sheets and documents: Change from "gpm"to USgpm
7 | Callout | 2 | Nalini Mohan | Intermittent operation, Refer to query T458 and 146 response
8 | Callout | 2 | hyunjin.paeng | Marine, dusty and corrosive
9 | Text Box | 2 | hyunjin.paeng | specify
10 | Callout | 2 | hyunjin.paeng | specify steam condition
11 | Callout | 2 | Dowon Pyun | To be corrected as '(22,24)'
12 | Callout | 2 | hyunjin.paeng | to be determined/confirmed according to pump supplier's datas
13 | Text Box | 3 | Nalini Mohan | All fields in the datasheet shall be filled. If the field is not applicable include as N/A
14 | Callout | 3 | Dowon Pyun | Note 10 deleted
15 | Callout | 3 | Isamu | Since first page and note 25 indicated manufacturer's standard .. line 3 shall read " Equivalent to API pump type VS4
16 | Text Box | 4 | Dowon Pyun | Data for pump mechanical seals shall be entered on BMPS-G-50302.
17 | Callout | 4 | Dowon Pyun | Note 16 deleted
18 | Callout | 6 | Nalini Mohan | Include correct drg no
19 | Callout | 6 | hyunjin.paeng | please attach sulphur pit dwg for vendor's reference
20 | Callout | 8 | Salman Jaffer | Check this number
21 | Callout | 8 | Syed Ahmed | In addition, and as normal practice, Pump shall be designed to empty out the Sulfur pit during T&I.
22 | Callout | 8 | Salman Jaffer | New numbering
23 | Callout | 8 | hyunjin.paeng | Stand by
24 | Callout | 8 | BD Mori | TTSJV shall provide the physical properties not the pump vendor. The pump vendor to design the pump for the given physical properties.