## 085-A-PFD-00001-001-RB
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Cloud+ | 1 | Ahmed Marhoon | AIT to be changed to AI on PFD. This was commented earlier and agreed but not implemented.
2 | Call-out | 1 | A.Jabbar Mahmood | As commented earlier in the previous issue: According to the H&MB and design basis, 10% of the "total CW make flow rate" is routed through the calcite beds. However, stream "B" does not represent the total make flowrate (total less the amount routed to the calcite beds) and hence A/B ratio will not be 10% (higher than 10%). TR to check and amend as necessary. Also rephrase the note for clarity. review the viability of relocating the F0005 to stream 1 to give direct measurement of the total Make-up flow and direct control of the flow ratio. TR to review and provide justification/explanation
3 | Cloud+ | 1 | A.Jabbar Mahmood | As commented earlier: Use a consistent representation of the pressure and temperature blocks i.e. circle above the rectangle
4 | Call-out | 1 | Sameer Foujdar | Backwash water supply line is routed to CSS. All the water will go to CSS no water will be going to the calcite bed during backwashing. TR to check the line up.
5 | Call-out | 1 | Sameer Foujdar | Battery limit to be shown in the PFD and note marked.
6 | Call-out | 1 | MAK | Change to 013 in all sheets.
7 | Cloud+ | 1 | Mohamed Ayyash | General comment: PFD preparation standard calls for stream names on the right side of the sheet to be aligned from the right side and not from left side. Need to correct all sheets.
8 | Call-out | 1 | MAK | General Comment: Use the predefined OPCs which are embedded as blocks in the latest drawing borders
9 | Cloud+ | 1 | Ahmed Marhoon | Review the direction of the arrows. Also review the requirement of LY/FY blocks.
10 | Call-out | 1 | 986131 | The response provided to the original query is not satisfactory - The overflow from the calcite bed can still be acidic (say when the calcite bed exhaust or channelling in the bed. If these goes directly to the CSS then it can lead to effluent quality not meeting the standard. All discharges from the calcite package can first go to a neutralising pit - any requirement to neutralize the discharge is facilitated in the area before the effluent can be sent to refinery CSS. Please review. How is the effluent from the curbed area planed to be neutralized before sending it out?
11 | Call-out | 1 | A.Jabbar Mahmood | THE TYPE OF THE TOP HEAD (FLAT HEAD) IS DIFFERENT THAN THAT DEPICTED ON THE PFDs (ELLIPTICAL). TR TO CHECK AND ENSURE CONSISTENCY. TYPICAL FOR ALL CALCITE BEDS
12 | Call-out | 1 | Ahmed Ali | there is no distinguishing between the two stream, name the first one Filtered CW Make-up