## 085-A-PID-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Abdulaziz | 1. Easy and safe maintenance access shall be provided for regular PM and major overhaul. 2. Jacking plate shall be provided for motor and G.Box to facilitate the alignment. 3. Mini lube oil station with pneumatic drum pump facility shall be provided for PM lubrication. 4. Oil drain facility to the ground level OSW shall be considered. 5. Maintenance removable platform shall be provided to facilitate the maintenance activities below G.Box level. Applicable for all CWT.
2 | Callout | 1 | Mohamed Ayyash | Add "Water" to the title
3 | Call-out | 1 | 986131 | Add the Equipment Data Blocks. If details are not available then a hold can be used against each such parameter.
4 | Call-out | 1 | 986131 | Add: From ......
5 | Text Box | 1 | Sameer Foujdar | All majority of the interconnecting PID for process flow and instrument logics are not correct. It is very difficult to review the document and flow the process flow. TR to review the transmittal correctly before submitting it to the owner for review. Transmittal to be corrected and resubmitted for review. This is applicable to all the sheet in this transmittal.
6 | Call-out | 1 | A.Jabbar Mahmood | Correct connector drawing number (085-A-PID-00024-001)
7 | Call-out | 1 | Hasan Al Noaimi | delete BMP
8 | Call-out | 1 | Hasan Al Noaimi | delete BMP
9 | Call-out | 1 | Mahdi Ali | Drawing not available for review
10 | Callout | 1 | Robert.Kawitzki | Equipment number as per BMPS-A8
11 | Call-out | 1 | Abdulaziz | Fan anti rotation mechanism shall be installed to prevent reverse rotation when fan is OOS. Applicable for all CWT.
12 | Call-out | 1 | Abdulaziz | Fan Motor and G.Box shall be connected to MCM for monitoring and protection. Applicable for all CWT.
13 | Text Box | 1 | Raj | General Comment for All Sheets: On these P&IDs there is a major issue with the P&ID Continuation sheet number reflected on each incoming/outgoing stream. Though some comments have been provided on the PID sheets, all PID sheets need to be re-submitted.
14 | Text Box | 1 | Mahdi Ali | General Comments 1. Use latest border that is part of the Homogenization procedure. 2. Scale of the drawing to be: NTS 3. Total Sheets to be in 3 digits, i.e 001 4. All equipment tags to have unit number as a prefix. This includes the tag numbers above the Off-page connectors. 5. ALL OFF PAGE CONNECTORS to BE VERIFIED
15 | Text Box | 1 | alexis.martinez | GENERAL: As per Symbology sheet BMPS-A-50003, the Buried lines to be shown on P&ID as dash lines.
16 | Call-out | 1 | Ahmed Ali | General: the correct numbering will be 085-A-PID-00005-001
17 | Text Box | 1 | A.Jabbar Mahmood | General: The majority of the drawing numbers indicated within the stream connector arrows are wrong. We assume that TR shall closely review this and ensure that all connector drawing numbers are correct.
18 | Call-out | 1 | 986131 | If this line is in the sump please represent it in the sump as the other chemicals and not close to the fan deck.
19 | Call-out | 1 | Mahdi Ali | Incorrect CONTINUATION
20 | Call-out | 1 | 986131 | indicate these as H1 to distinguish from the other notes. Applies to all P&ID.
21 | Callout | 1 | Mohamed Ayyash | Make this a General Note applicable to all sheets
22 | Callout | 1 | Mohamed Ayyash | Make this a General Note applicable to all sheets
23 | Text Box | 1 | A.Jabbar Mahmood | Means shall be provided to ensure even distribution of Chemicals to the CWT cells.
24 | Text Box | 1 | A.Jabbar Mahmood | Means shall be provided to ensure even distribution of CW to the CWT cells.
25 | Call-out | 1 | Sameer Foujdar | Note 15 to be deleted from all the 8 ball valves shown on OXYDANT BIOCIDE injection line as the same is covered with Note 6.
26 | Text Box | 1 | Ahmed Marhoon | Since the current revision of P&ID will be withdrawn and reissued as agreed with MOC, comments on instrumentation and control details will be provided on the next issue.
27 | Callout | 1 | Robert.Kawitzki | Text size to be as per BMPS-A8
28 | Callout | 1 | alexis.martinez | The 085-76"-CW-0036-B1-N to be shown on P&ID as dash line based on symbology sheet.
29 | Callout | 1 | Robert.Kawitzki | Title block to be completed
30 | Call-out | 1 | Abdulaziz | TR to ensure that in case of overflow the water stream shall be drained to a dedicated safe location to avoid splashing on the ground floor equipment. Applicable for all CWT.
31 | Call-out | 1 | 986131 | Update 50003 with the symbol
32 | Call-out | 1 | Ahmed Ali | use the correct unit name Cooling Water Tower CWT