## 085-A-PID-00002-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | A.Jabbar Mahmood | "CW SUPPLY TO P0001A/B/C"
2 | Call-out | 1 | A.Jabbar Mahmood | "Many" Stream connectors in this P&IDs have wrong referenced drawing number. TR is requested to check each stream connector and ensure correct drawing numbers are indicated.
3 | Call-out | 1 | Abdulaziz | 1. All measures shall be taken in to account to prevent ground water seepage. 2. Pump baseplate and associated pipe support shall be coated with corrosion resistance paint. 3. Pump pit room shall be furnished with pump out facility in case of any water leakage. Applicable for all pumps in cooling water tower service.
4 | Callout | 1 | Mohamed Ayyash | Add Note 6 indication here also
5 | Callout | 1 | Mohamed Ayyash | Add Note 6 indication here also
6 | Cloud+ | 1 | 986131 | Add the on the P&ID also.
7 | Call-out | 1 | 986131 | Cover with note the type of reducer.
8 | Cloud+ | 1 | Mohamed Ayyash | Delete space
9 | Call-out | 1 | Abdulaziz | Expansion rubber joint shall withstand pump shutoff pressure. Applicable for all pumps in cooling water tower service.
10 | Text Box | 1 | alexis.martinez | GENERAL: For pump discharge lines, concentric reducer can also be used.
11 | Text Box | 1 | Ahmed Ali | General: Most of the sheet numbers in the connections are wrong. Owner will not be able to review the document. Please correct and resend for review
12 | Text Box | 1 | A.Jabbar Mahmood | GENERAL: TR TO ENSURE THAT THE RIGHT LINE THICKNESS IS USED THROUGHOUT THE P&IDS AS PER BMPS
13 | Text Box | 1 | Ahmed Habib | Local
14 | Call-out | 1 | Sameer Foujdar | Note 14 is reference to entire concrete pit should be shown on the outside of the pit.
15 | Call-out | 1 | 986131 | Note 3 missing on the P&ID. please add.
16 | Call-out | 1 | Sameer Foujdar | Note 3 reference to be shown here.
17 | Callout | 1 | alexis.martinez | On note 4 add "Flat side to be located at the Top"
18 | Call-out | 1 | 986131 | Show symbol for eccentric reducer
19 | Callout | 1 | alexis.martinez | Shows as eccentric the reducers 66"x54" in pump suction as per note 4
20 | Call-out | 1 | Abdulaziz | TR to clarify the basis for 1.5 against API standard with respect to API standard.
21 | Call-out | 1 | Abdulaziz | TR to ensure easy access to perform any maintenance activities for the pump. Applicable for all pumps in cooling water tower service.
22 | Call-out | 1 | A.Jabbar Mahmood | TR to explain the rational for providing MOV on the discharge line only and not the suction line. This comment is typical for all pumps
23 | Call-out | 1 | Abdulaziz | Vortex breaker shall be considered for pump. Applicable for all pumps in cooling water tower service.